## Run Extract (hidden)
[12 empty] | 1 | 2 | 3 | 4 | 5 | 6
[12 empty] | Option 1 | Option 2 | Option 3 | Option 4 | Option 5 | Option 6
[10 empty] | Address | Value Metric | Option 1 Planned Stake impaired wood pole condition based | Option 2 Planned Replace an impaired pole with an S4 pole | Option 3 Planned replace impaired by a Titan FRC Pole | Option 4 Planned Topdown Budget Constraint Staking
[11 empty] | UARM - Environment and Community - Fire Risk | 31991574.3162 | 34284227.1954 | 34361491.3235 | 17334734.8488
[11 empty] | UARM - Safety & People - Worker | 16900116.5218 | 18111251.0541 | 18152067.1962 | 9157381.1416
Notes | [10 empty] | UARM - Network Performance Risk | 2739506202.4846 | 2935830918.839 | 2942447210.2481 | 1484410025.8785
Need to open the .xlsm Investment Summary report from Copperleaf in the Trusted folder Save in the preferred location as an .xlsx Need to test environment - other and when two of the same value models have been selected with a different name | [10 empty] | UARM - Environment and Community - Other Risk | 37356212.7025 | 40033318.4652 | 40123538.942 | 20241580.9771
[11 empty] | UARM - Financial Risk | 134557078.1144 | 144200013.0986 | 144524987.3065 | 72910174.6799
[11 empty] | UARM - Safety & People - Public | 50804449.2531 | 54445313.089 | 54568012.9576 | 27528550.1358
[11 empty] | Terminal Value | 10560866.2801 | 95047796.521 | 105608662.8011 | 5284003.4109
[11 empty] | Total Investment Cost | 23031072.803 | 201254521.7002 | 223532452.8124 | 11899638.667
Options
| Option | 2025 | 2026 | 2027 | 2028 | 2029
| Baseline | 316971551.72 | 347844109.73 | 380412616.18 | 414576289.75 | 450199229.74
| Option 1 Planned Stake impaired wood pole condition based | 299397713.54 | 312254188.5 | 324919565.46 | 337945106.04 | 351084427.32
| Option 2 Planned Replace an impaired pole with an S4 pole | 299397713.54 | 312254187.67 | 324919511.11 | 337944441.06 | 351080325.45
| Option 3 Planned replace impaired by a Titan FRC Pole | 299397713.54 | 312254187.64 | 324919509.35 | 337944419.56 | 351080192.84
| Option 4 Planned Topdown Budget Constraint Staking | 307667583.53 | 328948648.98 | 350874390.65 | 373785324.93 | 396833668.69
Option Breakdown | [7 empty] | Folder and File Paths
| Option 1 |  |  |  |  | Greater 0 | (Multiple Items)
| Recommended Option - Value | [6 empty] | This File Path | \\TNAD.tasnetworks.com.au\user$\user_folders\BahramabadiM\My Documents\Trusted\InvestmentTemplate.xlsm
| Value Function Measure | Value | Value in % | Greater 0 |  | Row Labels | Sum of Value in % | Folder Path | H:\RPSAM\SAM\R24 IES\final draft\
Option 1 | UARM - Environment and Community - Fire Risk | 31991.5743 | 1.05% | 1 | K20 | Terminal Value | 0.35% | File Name | InvestmentSummary_R24_D_OH_RESTK _Pole staking.xlsx
Option 1 | UARM - Safety & People - Worker | 16900.1165 | 0.56% | 1 | K21 | Total Investment Cost | 0.76% | File Path | H:\RPSAM\SAM\R24 IES\final draft\InvestmentSummary_R24_D_OH_RESTK _Pole staking.xlsx
Option 1 | UARM - Network Performance Risk | 2739506.2025 | 89.98% | 1 | K22 | UARM - Environment and Community - Fire Risk | 1.05%
Option 1 | UARM - Environment and Community - Other Risk | 37356.2127 | 1.23% | 1 | K23 | UARM - Environment and Community - Other Risk | 1.23%
Option 1 | UARM - Financial Risk | 134557.0781 | 4.42% | 1 | K24 | UARM - Financial Risk | 4.42%
Option 1 | UARM - Safety & People - Public | 50804.4493 | 1.67% | 1 | K25 | UARM - Network Performance Risk | 89.98%
Option 1 | Terminal Value | 10560.8663 | 0.35% | 1 | K26 | UARM - Safety & People - Public | 1.67%
Option 1 | Total Investment Cost | -23031.0728 | 0.76% | 1 | K27 | UARM - Safety & People - Worker | 0.56%
Option 1 |  |  |  | 0 | K28
Option 1 |  |  |  | 0 | K29
Option 1 |  |  |  | 0 | K30 |  |  | 1 | InvestmentSummary_R24_D_ND_PRHVR_Augment_HV_Fdr_TRIP.xlsx
Option 1 |  |  |  | 0 | K31 |  |  | 2 | InvestmentSummary_R24_D_OH_REPOL_Basic Fleet Pole Replacement.xlsx
Option 1 |  |  |  | 0 | K32 |  |  | 3 | InvestmentSummary_R24_T_ND_AUGSB_W Coast Reliability Improvement.xlsx
Option 1 |  |  |  | 0 | K33 |  |  | 4 | InvestmentSummary_R24_T_ND_AUGSB_Upper Derwent 110 kV Losses.xlsx
| Total | 2998645.4269 | 100% |  |  |  |  | 5 | InvestmentSummary_R24_D_OH_SIWES_Bird_Mitigation.xlsx
[8 empty] | 6 | InvestmentSummary_R24_D_SB_REGMS_GMS_Replacement of GMS.xlsx
[8 empty] | 7 | InvestmentSummary_R24_D_OH_REPOL_Complex Design.xlsx
Start | Option 1 |  |  |  |  | Greater 0 | 1 | 8 | InvestmentSummary_R24_D_PQ_PQTXV_Power_Quality_LV_Tformers.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 9 | InvestmentSummary_R24_D_ND_PQLVV_Aug_HV_LV_Conductor.xlsx
Option 1 | UARM - Environment and Community - Fire Risk | 31991.5743 | 1.05% | 1 | K20 | Row Labels | Sum of Value in % | 10 | InvestmentSummary_R24_D_CA_SOLCP_Crossover_Extension_OH.xlsx
Option 1 | UARM - Safety & People - Worker | 16900.1165 | 0.56% | 1 | K21 | Terminal Value | 0.35% | 11 | InvestmentSummary_R24_D_CI_SOIRR_Irrigation_Supply.xlsx
Option 1 | UARM - Network Performance Risk | 2739506.2025 | 89.98% | 1 | K22 | Total Investment Cost | 0.76% | 12 | InvestmentSummary_R24_D_AMIPD_AM Improvement Program.xlsx
Option 1 | UARM - Environment and Community - Other Risk | 37356.2127 | 1.23% | 1 | K23 | UARM - Environment and Community - Fire Risk | 1.05% | 13 | InvestmentSummary_R24_D_CI_SOPOR_Permanent_Residence_OH.xlsx
Option 1 | UARM - Financial Risk | 134557.0781 | 4.42% | 1 | K24 | UARM - Environment and Community - Other Risk | 1.23% | 14 | InvestmentSummary_R24_D_CI_SUPOR_Permanent_Residence_UG.xlsx
Option 1 | UARM - Safety & People - Public | 50804.4493 | 1.67% | 1 | K25 | UARM - Financial Risk | 4.42% | 15 | InvestmentSummary_R24_D_CI_SOGSI_General_Supply_OH.xlsx
Option 1 | Terminal Value | 10560.8663 | 0.35% | 1 | K26 | UARM - Network Performance Risk | 89.98% | 16 | InvestmentSummary_R24_D_CI_SUGSI_General_Supply_UG.xlsx
Option 1 | Total Investment Cost | -23031.0728 | 0.76% | 1 | K27 | UARM - Safety & People - Public | 1.67% | 17 | InvestmentSummary_R24_D_CI_SUSBD_Subdivision_UG.xlsx
Option 1 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.56% | 18 | InvestmentSummary_R24_D_CI_SOSDI_Subdivision_OH.xlsx
Option 1 |  |  |  | 0 | K29 |  |  | 19 | InvestmentSummary_R24_D_CI_SUSUB_Augment_Dist_Substations.xlsx
Option 1 |  |  |  | 0 | K30 |  |  | 20 | InvestmentSummary_R24_T_ND_LAEMP_SELA.xlsx
Option 1 |  |  |  | 0 | K31 |  |  | 21 | InvestmentSummary_R24_D_CA_DESDB_Prelim_Drive_by_Design.xlsx
Option 1 |  |  |  | 0 | K32 |  |  | 22 | InvestmentSummary_R24_D_CI_SUMPR_Major_Commercial.xlsx
Option 1 |  |  |  | 0 | K33 |  |  | 23 | InvestmentSummary_R24_D_CI_EASEN_Easements_Non_Major_Comm.xlsx
| Total | 2998645.4269 | 100% |  |  |  |  | 24 | InvestmentSummary_R24_D_ND_PRHVR_Rosebery_Supply_Improve.xlsx
[8 empty] | 25 | InvestmentSummary_R24_D_ND_CAHVF_Huonville_Supply_Improvement.xlsx
[8 empty] | 26 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Fdr_Network_Access.xlsx
[8 empty] | 27 | InvestmentSummary_R24_D_ND_PRHVR_Deloraine_Supply_Improve.xlsx
| Option 2 |  |  |  |  | Greater 0 | 1 | 28 | InvestmentSummary_R24_D_ND_CALVF_Augment_LV_Fdr_Capacity.xlsx
| Value Function Measure | Value | Value in % | Greater 0 |  |  |  | 29 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Trunk.xlsx
Option 2 | UARM - Environment and Community - Fire Risk | 34284.2272 | 0.97% | 1 | K20 | Row Labels | Sum of Value in % | 30 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Pole_Mtd_Regulator.xlsx
Option 2 | UARM - Safety & People - Worker | 18111.2511 | 0.51% | 1 | K21 | Terminal Value | 2.7% | 31 | InvestmentSummary_R24_D_ND_CAHVF_Aug_Grnd_Mtd_Regulator.xlsx
Option 2 | UARM - Network Performance Risk | 2935830.9188 | 83.33% | 1 | K22 | Total Investment Cost | 5.71% | 32 | InvestmentSummary_R24_D_ND_CAHVF_22kV_Emu_Bay_Feeders.xlsx
Option 2 | UARM - Environment and Community - Other Risk | 40033.3185 | 1.14% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0.97% | 33 | InvestmentSummary_R24_D_ND_CAHVF_Augment_HV_Fdr_Capacity.xlsx
Option 2 | UARM - Financial Risk | 144200.0131 | 4.09% | 1 | K24 | UARM - Environment and Community - Other Risk | 1.14% | 34 | InvestmentSummary_R24_D_ND_CAHVF_Aug_SubStd_Cond_Capacity.xlsx
Option 2 | UARM - Safety & People - Public | 54445.3131 | 1.55% | 1 | K25 | UARM - Financial Risk | 4.09% | 35 | InvestmentSummary_R24_D_ND_LANDZ_LandAcq_ZoneSubs.xlsx
Option 2 | Terminal Value | 95047.7965 | 2.7% | 1 | K26 | UARM - Network Performance Risk | 83.33% | 36 | InvestmentSummary_R24_D_ND_CATXU_Aug_Dist_Sub.xlsx
Option 2 | Total Investment Cost | -201254.5217 | 5.71% | 1 | K27 | UARM - Safety & People - Public | 1.55% | 37
Option 2 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.51% | 38
Option 2 |  |  |  | 0 | K29 |  |  | 39
Option 2 |  |  |  | 0 | K30 |  |  | 40
Option 2 |  |  |  | 0 | K31 |  |  | 41
Option 2 |  |  |  | 0 | K32 |  |  | 42
Option 2 |  |  |  | 0 | K33 |  |  | 43
| Total | 3120698.3166 | 100%
| Option 3 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 3 | UARM - Environment and Community - Fire Risk | 34361.4913 | 0.96% | 1 | K20 | Row Labels | Sum of Value in %
Option 3 | UARM - Safety & People - Worker | 18152.0672 | 0.51% | 1 | K21 | Terminal Value | 2.96%
Option 3 | UARM - Network Performance Risk | 2942447.2102 | 82.58% | 1 | K22 | Total Investment Cost | 6.27%
Option 3 | UARM - Environment and Community - Other Risk | 40123.5389 | 1.13% | 1 | K23 | UARM - Environment and Community - Fire Risk | 0.96%
Option 3 | UARM - Financial Risk | 144524.9873 | 4.06% | 1 | K24 | UARM - Environment and Community - Other Risk | 1.13%
Option 3 | UARM - Safety & People - Public | 54568.013 | 1.53% | 1 | K25 | UARM - Financial Risk | 4.06%
Option 3 | Terminal Value | 105608.6628 | 2.96% | 1 | K26 | UARM - Network Performance Risk | 82.58%
Option 3 | Total Investment Cost | -223532.4528 | 6.27% | 1 | K27 | UARM - Safety & People - Public | 1.53%
Option 3 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.51%
Option 3 |  |  |  | 0 | K29
Option 3 |  |  |  | 0 | K30
Option 3 |  |  |  | 0 | K31
Option 3 |  |  |  | 0 | K32
Option 3 |  |  |  | 0 | K33
| Total | 3116253.518 | 100%
| Option 4 |  |  |  |  | Greater 0 | 1
| Value Function Measure | Value | Value in % | Greater 0
Option 4 | UARM - Environment and Community - Fire Risk | 17334.7348 | 1.05% | 1 | K20 | Row Labels | Sum of Value in %
Option 4 | UARM - Safety & People - Worker | 9157.3811 | 0.56% | 1 | K21 | Terminal Value | 0.32%
Option 4 | UARM - Network Performance Risk | 1484410.0259 | 90.03% | 1 | K22 | Total Investment Cost | 0.72%
Option 4 | UARM - Environment and Community - Other Risk | 20241.581 | 1.23% | 1 | K23 | UARM - Environment and Community - Fire Risk | 1.05%
Option 4 | UARM - Financial Risk | 72910.1747 | 4.42% | 1 | K24 | UARM - Environment and Community - Other Risk | 1.23%
Option 4 | UARM - Safety & People - Public | 27528.5501 | 1.67% | 1 | K25 | UARM - Financial Risk | 4.42%
Option 4 | Terminal Value | 5284.0034 | 0.32% | 1 | K26 | UARM - Network Performance Risk | 90.03%
Option 4 | Total Investment Cost | -11899.6387 | 0.72% | 1 | K27 | UARM - Safety & People - Public | 1.67%
Option 4 |  |  |  | 0 | K28 | UARM - Safety & People - Worker | 0.56%
Option 4 |  |  |  | 0 | K29
Option 4 |  |  |  | 0 | K30
Option 4 |  |  |  | 0 | K31
Option 4 |  |  |  | 0 | K32
Option 4 |  |  |  | 0 | K33
| Total | 1624966.8124 | 100%
| Option 5 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 5 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 5 |  |  |  | 0 | K21 |  | 0%
Option 5 |  |  |  | 0 | K22
Option 5 |  |  |  | 0 | K23
Option 5 |  |  |  | 0 | K24
Option 5 |  |  |  | 0 | K25
Option 5 |  |  |  | 0 | K26
Option 5 |  |  |  | 0 | K27
Option 5 |  |  |  | 0 | K28
Option 5 |  |  |  | 0 | K29
Option 5 |  |  |  | 0 | K30
Option 5 |  |  |  | 0 | K31
Option 5 |  |  |  | 0 | K32
Option 5 |  |  |  | 0 | K33
| Total | 0 | 0%
| Option 6 |  |  |  |  | Greater 0 | 0
| Value Function Measure | Value | Value in % | Greater 0
Option 6 |  |  |  | 0 | K20 | Row Labels | Sum of Value in %
Option 6 |  |  |  | 0 | K21 |  | 0%
Option 6 |  |  |  | 0 | K22
Option 6 |  |  |  | 0 | K23
Option 6 |  |  |  | 0 | K24
Option 6 |  |  |  | 0 | K25
Option 6 |  |  |  | 0 | K26
Option 6 |  |  |  | 0 | K27
Option 6 |  |  |  | 0 | K28
Option 6 |  |  |  | 0 | K29
Option 6 |  |  |  | 0 | K30
Option 6 |  |  |  | 0 | K31
Option 6 |  |  |  | 0 | K32
Option 6 |  |  |  | 0 | K33
| Total | 0 | 0%

## Summary
Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | NPV Period | Base Fiscal Year | Currency Scale
|  |  |  | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
|  |  |  | Investment Name | [5 empty] | Scenario
|  |  |  | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
Value Function |  | TasNetworks Value Function |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Investment Description
Description |  | Pole staking is a safe and affordable alternative option to pole replacement, which manages the risk of pole failures. Staking an impaired wood pole restores pole safety and defers full pole replacement for approximately 10 to 15 years. | [9 empty] | TRUE
Functional Area |  | RESTK |  |  | Department |  |  | Asset Strategy
Works Initiator |  |  |  |  | Portfolio |  |  | Dx - Renewal
Investment Category |  | Prescribed Services - Asset Renewal |  |  | Needs Item Reference
Investment Type |  | Network Project |  |  | Document No. |  |  | R2355521
Investment Stage |  | Gate 2 – Investment Evaluation Summary |  |  | Project Zone Location
PPM ID |  |  |  |  | Regulatory Test Required |  |  | No
Investment Summary
Problem Definition |  | Analysis of the performance of the wood pole population has confirmed that performance has not materially deteriorated. Notwithstanding the reasonable performance levels realised to date, additional investment will be required in future years to sustain the performance of the wood pole population and to ensure the number of poles at or exceeding their service life remains manageable. In particular, a plan is required to extend the service life of class S3 wood poles whilst completing the transition to alternative bushfire resistant poles, such as Fibreglass Reinforced Composite (FRC) poles (i.e.: Titan poles) due to an increasing shortage of class S3 wood poles. | [9 empty] | TRUE
Recommendation |  | Option 1 (Planned Stake impaired wood pole condition based) is recommended for approval as it best satisfies the customer and business needs. | [9 empty] | TRUE
Alternative Spend Profile
Name |  | Status | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV | Alternative Start Date
Option 1 Planned Stake impaired wood pole condition based |  | Recommended | 1529000 | 1529000 | 1529000 | 1529000 | 1529000 | 7645000 | 32109000 | 2998645426.87 | 4547400%
Option 2 Planned Replace an impaired pole with an S4 pole |  | Candidate | 13361000 | 13361000 | 13361000 | 13361000 | 13361000 | 66805000 | 280581000 | 3120698316.56 | 4547400%
Option 3 Planned replace impaired by a Titan FRC Pole |  | Candidate | 14840000 | 14840000 | 14840000 | 14840000 | 14840000 | 74200000 | 311640000 | 3116253517.96 | 4547400%
Option 4 Planned Topdown Budget Constraint Staking |  | Candidate | 790000 | 790000 | 790000 | 790000 | 790000 | 3950000 | 16590000 | 1624966812.41 | 4547400%
0
0
Leader Endorsement
Name |  |  | Governance |  | Signature |  |  | Comments |  |  | Date
|  |  | Submission | [7 empty] | 4486500%
|  |  | Endorsement | [7 empty] | 4486500%
|  |  | Approval | [7 empty] | 4486500%
Investment Attachments
Date | Attachment Name |  | Description

## Investment Overview
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000500 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_OH_RESTK _Pole staking |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-31
Functional Area | RESTK |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R2355521
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks has approximately 240,000 support structures installed on the distribution network to provide support, insulation and adequate clearances between live electrical and the ground, vegetation and building infrastructure. Wood poles deteriorate at a greater rate below or near the ground line compared to higher above the ground, primarily because of greater water availability for biological wood rot growth. Thus, the above ground section may have many more years of useful service remaining when the below ground section has deteriorated. Stakes (or ground-line reinforcing) may be installed on wood poles to strengthen the pole at and below ground level. Staking wood poles commenced in 2002 and the current staked wood pole population is approximately 29,000 poles. Wood poles are generally staked at 30-45 years of age with the staking process typically extending the life of a wood pole by a further 10-15 years. Staking wood poles has proven to be a cost-effective way of ensuring the service life of 40-50 years is attained. |  |  |  |  | TRUE
| Problem Definition |  | Analysis of the performance of the wood pole population has confirmed that performance has not materially deteriorated. Notwithstanding the reasonable performance levels realised to date, additional investment will be required in future years to sustain the performance of the wood pole population and to ensure the number of poles at or exceeding their service life remains manageable. In particular, a plan is required to extend the service life of class S3 wood poles whilst completing the transition to alternative bushfire resistant poles, such as Fibreglass Reinforced Composite (FRC) poles (i.e.: Titan poles) due to an increasing shortage of class S3 wood poles. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; - supply reliability and safety of the current network; - resilience to future impacts including climate change; and - investment in future networks to unlock community benefits in renewable energy products and services. |  |  |  |  | TRUE

## Objectives and Analysis
Investment Evaluation Summary |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000500 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_OH_RESTK _Pole staking |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-31
Functional Area | RESTK |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R2355521
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Objectives and Analysis
03. Business Performance Objectives | Safety and Wellbeing |  | Performance Measure: Significant incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. Performance Measure: Reportable incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. |  |  |  |  | TRUE
| Our Customers |  | Performance Measure: Customer net promoter score Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. |  |  |  |  | FALSE
| Our People |  | Performance Measure: Employee engagement Investment impact on performance: Maintain our vision of ‘powering a bright future.’ |  |  |  |  | FALSE
| Our Business - Sustained Cost Management |  | Performance Measure: Capital expenditure Investment impact on performance: Replacement reduces our total cost when compared to managing end of life pole failures. Performance Measure: Operational expenditure Investment impact on performance: Replacement reduces our operational cost in replacing poles in poor condition in a planned way prior to failure. |  |  |  |  | FALSE
| Our Business - Network Service |  | Performance Measure: Service incentive bonuses earned - distribution. Investment impact on performance: Replacement of poles will reduce the risk of failure and therefore minimise prolonged outages. |  |  |  |  | FALSE
04. Business Risks | Death or Injury (Employee) |  | Employee impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. |  |  |  |  | FALSE
| Death or Injury (Public) |  | Public impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. |  |  |  |  | FALSE
| Sustainable and Predictable Pricing |  | If a sustainable proactive program is not implemented, increased failure rates will result in a large increase in the program of work and ultimately increase power price to customer. |  |  |  |  | FALSE
| Widespread Power Disruption |  | An average of 10 unassisted pole failures occur per year currently. |  |  |  |  | FALSE
| Bushfire Start |  | TasNetworks has recorded ground fire starts from pole failures. |  |  |  |  | FALSE
| Loss of Major Industrial | [6 empty] | FALSE
| Customer Focus |  | Customers have an expectation of consistent and reliable power supply which these assets provide. |  |  |  |  | FALSE
| Business Continuity Management | [6 empty] | FALSE
| Cyber Security | [6 empty] | FALSE
| Private Assets | [6 empty] | FALSE
Energy Policy and Regulation
Project Marinus (D&A)
Tasmanian Power System Complexity
| Emerging Complexity of the NEM | [6 empty] | FALSE
05. Strategic Objectives | Strategic Objectives |  | The strategic objective is to manage the risk to customers by developing a risk based strategic plan. This includes a condition/risk-based approach to manage the assets to maintain reliability and security of the network and effectively manage the safety and bushfire risk associated with maintaining the asset. |  |  |  |  | FALSE
| Strategic Document #1 |  | Towards 2030 We continually assess what value means to our customers to better serve all our stakeholders: Ensuring our electricity network remains resilient and fit-for-purpose by proactively maintaining assets, designing out risks, and making prudent investments of long-term value: The long-term impact of asset maintenance and renewal has been reviewed out to 2050. The analysis clearly demonstrates work should be done to mitigate risks to customers now and into the future. To ensure our capital is used wisely, we will streamline our investment planning to achieve optimised investment strategies and have the best delivery model: Investment planning has been developed to align all asset categories. The plan has been developed out to 2050 to ensure the long-term objectives of optimising investment strategies is achieved. |  |  |  |  | FALSE
| Strategic Document #2 |  | TasNetworks Business Plan |  |  |  |  | FALSE
| Strategic Document #3 |  | Bushfire Risk Mitigation Plan |  |  |  |  | FALSE
| Strategic Document #4 |  | Overhead Line Support Structures Asset Management Plan |  |  |  |  | FALSE
| Strategic Document #5 | [6 empty] | FALSE
06. Project Objectives | Project Objectives |  | The objective of this project is to implement a safe and affordable program that manages the risk of pole failures and provides an alternative to traditional pole replacements. Staking impaired wood poles that are suitable for staking restores pole safety and defers full capital cost of pole replacement for 10 to 15 years. With increasing shortage of class S3 wood poles, a plan is required to extend the service life of class S3 wood poles whilst completing the transition to alternative bushfire resistant poles (currently FRC Titans). |  |  |  |  | FALSE
07. Options Analysis | Benchmarking |  | Western Power Wood Poles Audit (2013), Report2013_17-Western-Power-Wood-Poles.pdf (audit.wa.gov.au). ESV Pole Inspection Audit of Powercor (2019). ESV investigation requires safety improvements for Powercor pole regime – Energy Safe Victoria. |  |  |  |  | TRUE
| Expert Findings |  | Expert analysis is used to design and assess the condition of wood poles. These findings are then used to develop TasNetworks asset management strategies. Examples of these resources are: - Australian Standard for Design of Overhead Lines AS/NZS 7000 - 2016; - SAA HB 331:2020 Overhead Design Manual ; - Economic Evaluation of Treated Wooden Pole Inspection Cycles (R295189); - Network Policy NN R AM 11 Wood pole reinstatement by ground-line reinforcement (NW10149727); - ENA DOC 015-2006 National Guidelines for Prevention of Unauthorised Access to Electricity Infrastructure; - Nathan Spencer, Leith Elder, Pole Service Life - An analysis of Country Energy Data , White Paper it is published accessible on http://www.koppers.com.au/Utility-Poles/default.aspx; - Timber – Natural Durability Ratings AS 5604 – 2005; - UTAS Final Report Identification of soft rot decay fungi in eucalypt power pole samples( R 719238); and - Energy Network Association (ENA) Pole Fire Test. |  |  |  |  | FALSE
08. Investment Timing | Investment Timing |  | The program will continue for the whole regulatory period and beyond to manage and flatten forecast pole replacement volumes to a manageable level. |  |  |  |  | TRUE
09. Expected Outcomes and Benefits | Expected Outcomes and Benefits |  | The benefits to TasNetworks from implementation of the recommended option will be: - longer asset service life for wood poles; - reduced capital expenditure required to maintain wood pole fleet (with resulting reduced average unit rate for RIN benchmarking); - maintain unassisted and assisted pole failure rates; and - staked wood poles remain vulnerable to bushfire risks. |  |  |  |  | TRUE
10. Assumptions | Assumptions |  | Staking extends pole service life by 10-15 years. FRC /Titan pole service life expectancy is 65 years. The service life expectation of plantation grown timber, will be no better than a local native species class S4, based on observed short service life of similar class S2 species imported from intestate. |  |  |  |  | TRUE
11. Regulatory Considerations | Regulatory Investment Test |  | A RIT-D is not required because this is a high volume, low cost, program with separate sites identified where assets have failed a serviceability test by asset inspection and this program is an alternative to full asset replacement.
| Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | No
| Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
| Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). |  | Yes
12. Recommendation | Recommendation |  | Option 1 (Planned Stake impaired wood pole condition based) is recommended for approval as it best satisfies the customer and business needs. |  |  |  |  | TRUE

## Economic Analysis
alternative
| Investment Evaluation Summary |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[5 empty] | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
[5 empty] | Investment Name | [5 empty] | Scenario
[5 empty] | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
autofit | Value Function |  |  | TasNetworks Value Function | Version |  | 0.1 |  | Date |  | 2022-10-31
Economic Analysis
| Parameter |  |  |  | Value | Unit | Source of Values
75679 | NPV Period |  |  |  | 25 | Years | TasNetworks requirement
autofit | First Fiscal Year of Forecast |  |  |  | FY23 | - | TasNetworks requirement
| Weighted Average Cost of Capital (WACC) |  |  |  | 2.82 | % | 2019-24 Revenue determination and ISP 2022 draft data
| Voluntary load shedding assumed? |  |  |  | No | - | N/A
| Reduction in system losses considered? |  |  |  | No | - | N/A
| Value of Customer Reliability applied |  |  | Very large business customer - Services | 10.93 | $/kWh | AER - Values of Customer Reliability - Annual adjustment summary - December 2021
|  |  |  | Residential | 17.08 | $/kWh
|  |  |  | Very large business customer - Metals | 20.6 | $/kWh
|  |  |  | Very large business customer - Transmission | 27.43 | $/kWh
|  |  |  | Very large business customer - Mines | 36.47 | $/kWh
|  |  |  | Business customer - Agricultural | 39.28 | $/kWh
|  |  |  | Business customer - Commercial | 46.18 | $/kWh
|  |  |  | Very large business customer - Distribution | 58.8 | $/kWh
|  |  |  | Business customer - Industrial | 66.16 | $/kWh
autofit |  |  |  | Very large business customer - Industrial | 122.39 | $/kWh
Sensitivity to Project Timing
|  | 1 | Navigate to Copperleaf Portfolio and search for your Investment
|  | 2 | Navigate to the Value Comparison Page for your Investment through the breadcrumb menu
|  | 3 | Once on the Value Comparison Page, select "Value by Start Date" in the drop-down menu in the top-left corner of the page
|  | 4 | This screen will show the value change over time for each option in your investment
|  | 5 | With the snipping tool on your PC, take a screenshot of the chart and copy + paste it in this section of the report
Options Considered
| Options Summary |  |  |  | R24 Expenditure ($M) | NPV ($M) | Preferred Option | Reason for selection/rejection
| Option 1 Planned Stake impaired wood pole condition based |  |  |  | 7.645 | 2998.6454 | Yes | This option has been selected as it has a similar NPV value compared to pole replacement options with a significantly lower capital expenditure. This option effectively manages the risk of unassisted pole failure, maintains network reliability and reduces the lifecycle costs of distribution support structures.
| Option 2 Planned Replace an impaired pole with an S4 pole |  |  |  | 66.805 | 3120.6983 | No | This option is rejected due to significant increase in capital expenditure and does not meet the business nor customer needs to manage affordability.
| Option 3 Planned replace impaired by a Titan FRC Pole |  |  |  | 74.2 | 3116.2535 | No | This option is rejected due to significant increase in capital expenditure and does not meet the business nor customer needs to manage affordability. Portfolio optimisation identified that the increased bushfire resilience provided by the use of Titan FRC poles is outweighed by the increased cost of pole replacements.
| Option 4 Planned Topdown Budget Constraint Staking |  |  |  | 3.95 | 1624.9668 | No | This option was rejected after portfolio optimisation to assess risk and expenditure across the whole asset portfolio. It has the lowest NPV and does not manage risk effectively compared to the other options.
0
0
NPV Components

## Needs Assessment (hidden)
Needs Assessment Form |  | Copperleaf Investment Code |  | Report Start Year | NPV Period | Base Fiscal Year | Currency Scale
|  | PRJ000500 |  | 2025 | 25 | FY23 | Literal
|  | Investment Name |  |  |  |  | Scenario
|  | R24_D_OH_RESTK _Pole staking |  |  |  |  | Approved
Value Function | TasNetworks Value Function | Version |  | 0.1 | Date |  | 2022-10-31
Functional Area | RESTK |  | Department |  | Asset Strategy
Works Initiator |  |  | Portfolio |  | Dx - Renewal
Investment Category | Prescribed Services - Asset Renewal |  | Needs Item Reference
Investment Type | Network Project |  | Document No. |  | R2355521
Investment Stage | Gate 2 – Investment Evaluation Summary |  | Project Zone Location
PPM ID |  |  | Regulatory Test Required |  | No
Investment Overview
01. Overview | Background |  | TasNetworks has approximately 240,000 support structures installed on the distribution network to provide support, insulation and adequate clearances between live electrical and the ground, vegetation and building infrastructure. Wood poles deteriorate at a greater rate below or near the ground line compared to higher above the ground, primarily because of greater water availability for biological wood rot growth. Thus, the above ground section may have many more years of useful service remaining when the below ground section has deteriorated. Stakes (or ground-line reinforcing) may be installed on wood poles to strengthen the pole at and below ground level. Staking wood poles commenced in 2002 and the current staked wood pole population is approximately 29,000 poles. Wood poles are generally staked at 30-45 years of age with the staking process typically extending the life of a wood pole by a further 10-15 years. Staking wood poles has proven to be a cost-effective way of ensuring the service life of 40-50 years is attained. |  |  |  |  | TRUE
| Problem Definition |  | Analysis of the performance of the wood pole population has confirmed that performance has not materially deteriorated. Notwithstanding the reasonable performance levels realised to date, additional investment will be required in future years to sustain the performance of the wood pole population and to ensure the number of poles at or exceeding their service life remains manageable. In particular, a plan is required to extend the service life of class S3 wood poles whilst completing the transition to alternative bushfire resistant poles, such as Fibreglass Reinforced Composite (FRC) poles (i.e.: Titan poles) due to an increasing shortage of class S3 wood poles. |  |  |  |  | FALSE
02. Customer Needs and Impact | Customer Needs and impact |  | TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; - supply reliability and safety of the current network; - resilience to future impacts including climate change; and - investment in future networks to unlock community benefits in renewable energy products and services. |  |  |  |  | TRUE
03. Business Objectives | Business Objectives
04. Project Objectives | Project Objectives |  | The objective of this project is to implement a safe and affordable program that manages the risk of pole failures and provides an alternative to traditional pole replacements. Staking impaired wood poles that are suitable for staking restores pole safety and defers full capital cost of pole replacement for 10 to 15 years. With increasing shortage of class S3 wood poles, a plan is required to extend the service life of class S3 wood poles whilst completing the transition to alternative bushfire resistant poles (currently FRC Titans). |  |  |  |  | FALSE
05. Risk Objective | Risk if not progressed | [6 empty] | TRUE
06. Investment Timing | Investment Timing |  | The program will continue for the whole regulatory period and beyond to manage and flatten forecast pole replacement volumes to a manageable level. |  |  |  |  | TRUE
07. Business Consulatation | Business Consulatation | [6 empty] | TRUE

## Option 1
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Option 1 Planned Stake impaired wood pole condition based
autofit | Description |  | Pole staking is a safe and affordable alternative program to defer full pole replacement, which manages the risk of pole failures and provides an alternative to traditional pole replacements. Staking an impaired wood pole that is suitable for the staking method, restores the pole safety and defers full capital cost of pole replacement whilst the transition to alternative pole types is fully implemented.
autofit | Alternative Status |  | Recommended
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option has been selected as it has a similar NPV value compared to pole replacement options with a significantly lower capital expenditure. This option effectively manages the risk of unassisted pole failure, maintains network reliability and reduces the lifecycle costs of distribution support structures.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 1 Planned Stake impaired wood pole condition based |  | Capex |  |  | 1479000 | 1479000 | 1479000 | 1479000 | 1479000 | 7395000 | 32109000 | 2998645426.87
|  |  | Opex |  |  | 50000 | 50000 | 50000 | 50000 | 50000 | 250000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 31991.5743 | 1.05%
[9 empty] | UARM - Safety & People - Worker |  |  | 16900.1165 | 0.56%
[9 empty] | UARM - Network Performance Risk |  |  | 2739506.2025 | 89.98%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 37356.2127 | 1.23%
[9 empty] | UARM - Financial Risk |  |  | 134557.0781 | 4.42%
[9 empty] | UARM - Safety & People - Public |  |  | 50804.4493 | 1.67%
[9 empty] | Terminal Value |  |  | 10560.8663 | 0.35%
[9 empty] | Total Investment Cost |  |  | -23031.0728 | 0.76%
[9 empty] | Total |  |  | 2998645.4269
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 1479000 | 1479000 | 1479000 | 1479000 | 1479000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 50000 | 50000 | 50000 | 50000 | 50000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -23031.0728 | Dollar | 1529000 | 1529000 | 1529000 | 1529000 | 1529000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 10560.8663 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 31991.5743 | Dollar | 3180948.65 | 3317542.17 | 3452105.36 | 3590495.12 | 3730093.73
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 16900.1165 | Dollar | 1680392.54 | 1752550.48 | 1823635.88 | 1896742.72 | 1970488.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 2739506.2025 | Dollar | 272391363.57 | 284088155.46 | 295611086.82 | 307461694.21 | 319415819.03
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 3932381.93 | 4315390.08 | 4719438.35 | 5143276.43 | 5585218.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 37356.2127 | Dollar | 3714359.07 | 3873857.83 | 4030985.81 | 4192582.02 | 4355589.8
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 14164439.71 | 15544035.08 | 16999416.94 | 18526081.69 | 20117956.36
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 134557.0781 | Dollar | 13379121.37 | 13953635.91 | 14519610.89 | 15101680.43 | 15688834.46
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 50804.4493 | Dollar | 5051528.34 | 5268446.65 | 5482140.7 | 5701911.54 | 5923602.13
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 316971551.72 | 347844109.73 | 380412616.18 | 414576289.75 | 450199229.74
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 299397713.54 | 312254188.5 | 324919565.46 | 337945106.04 | 351084427.32
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 2
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Option 2 Planned Replace an impaired pole with an S4 pole
autofit | Description |  | This option ceases the pole staking program and increases pole replacement volumes with class S4 wood poles.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option is rejected due to significant increase in capital expenditure and does not meet the business nor customer needs to manage affordability.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 2 Planned Replace an impaired pole with an S4 pole |  | Capex |  |  | 13311000 | 13311000 | 13311000 | 13311000 | 13311000 | 66555000 | 280581000 | 3120698316.56
|  |  | Opex |  |  | 50000 | 50000 | 50000 | 50000 | 50000 | 250000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 34284.2272 | 0.97%
[9 empty] | UARM - Safety & People - Worker |  |  | 18111.2511 | 0.51%
[9 empty] | UARM - Network Performance Risk |  |  | 2935830.9188 | 83.33%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 40033.3185 | 1.14%
[9 empty] | UARM - Financial Risk |  |  | 144200.0131 | 4.09%
[9 empty] | UARM - Safety & People - Public |  |  | 54445.3131 | 1.55%
[9 empty] | Terminal Value |  |  | 95047.7965 | 2.7%
[9 empty] | Total Investment Cost |  |  | -201254.5217 | 5.71%
[9 empty] | Total |  |  | 3120698.3166
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 13311000 | 13311000 | 13311000 | 13311000 | 13311000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 50000 | 50000 | 50000 | 50000 | 50000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -201254.5217 | Dollar | 13361000 | 13361000 | 13361000 | 13361000 | 13361000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 95047.7965 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 34284.2272 | Dollar | 3180948.65 | 3317542.16 | 3452104.79 | 3590488.05 | 3730050.15
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 18111.2511 | Dollar | 1680392.54 | 1752550.48 | 1823635.58 | 1896738.99 | 1970465.14
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 2935830.9188 | Dollar | 272391363.57 | 284088154.7 | 295611037.35 | 307461089.22 | 319412087.17
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 3932381.93 | 4315390.08 | 4719438.35 | 5143276.43 | 5585218.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 40033.3185 | Dollar | 3714359.07 | 3873857.82 | 4030985.14 | 4192573.77 | 4355538.91
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 14164439.71 | 15544035.08 | 16999416.94 | 18526081.69 | 20117956.36
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 144200.0131 | Dollar | 13379121.37 | 13953635.87 | 14519608.46 | 15101650.71 | 15688651.16
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 54445.3131 | Dollar | 5051528.34 | 5268446.64 | 5482139.79 | 5701900.32 | 5923532.92
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 316971551.72 | 347844109.73 | 380412616.18 | 414576289.75 | 450199229.74
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 299397713.54 | 312254187.67 | 324919511.11 | 337944441.06 | 351080325.45
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 3
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Option 3 Planned replace impaired by a Titan FRC Pole
autofit | Description |  | This option ceases the pole staking program and increases pole replacement volumes with titan FRC poles for increased bushfire resilience.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option is rejected due to significant increase in capital expenditure and does not meet the business nor customer needs to manage affordability. Portfolio optimisation identified that the increased bushfire resilience provided by the use of Titan FRC poles is outweighed by the increased cost of pole replacements.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 3 Planned replace impaired by a Titan FRC Pole |  | Capex |  |  | 14790000 | 14790000 | 14790000 | 14790000 | 14790000 | 73950000 | 311640000 | 3116253517.96
|  |  | Opex |  |  | 50000 | 50000 | 50000 | 50000 | 50000 | 250000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 34361.4913 | 0.96%
[9 empty] | UARM - Safety & People - Worker |  |  | 18152.0672 | 0.51%
[9 empty] | UARM - Network Performance Risk |  |  | 2942447.2102 | 82.58%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 40123.5389 | 1.13%
[9 empty] | UARM - Financial Risk |  |  | 144524.9873 | 4.06%
[9 empty] | UARM - Safety & People - Public |  |  | 54568.013 | 1.53%
[9 empty] | Terminal Value |  |  | 105608.6628 | 2.96%
[9 empty] | Total Investment Cost |  |  | -223532.4528 | 6.27%
[9 empty] | Total |  |  | 3116253.518
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 14790000 | 14790000 | 14790000 | 14790000 | 14790000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 50000 | 50000 | 50000 | 50000 | 50000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -223532.4528 | Dollar | 14840000 | 14840000 | 14840000 | 14840000 | 14840000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 105608.6628 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 34361.4913 | Dollar | 3180948.65 | 3317542.16 | 3452104.77 | 3590487.82 | 3730048.74
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 18152.0672 | Dollar | 1680392.54 | 1752550.48 | 1823635.57 | 1896738.87 | 1970464.4
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 2942447.2102 | Dollar | 272391363.57 | 284088154.67 | 295611035.75 | 307461069.66 | 319411966.52
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 3932381.93 | 4315390.08 | 4719438.35 | 5143276.43 | 5585218.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 40123.5389 | Dollar | 3714359.07 | 3873857.82 | 4030985.12 | 4192573.5 | 4355537.27
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 14164439.71 | 15544035.08 | 16999416.94 | 18526081.69 | 20117956.36
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 144524.9873 | Dollar | 13379121.37 | 13953635.87 | 14519608.38 | 15101649.75 | 15688645.23
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 54568.013 | Dollar | 5051528.34 | 5268446.64 | 5482139.76 | 5701899.96 | 5923530.68
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 316971551.72 | 347844109.73 | 380412616.18 | 414576289.75 | 450199229.74
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 299397713.54 | 312254187.64 | 324919509.35 | 337944419.56 | 351080192.84
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 4
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name |  | Option 4 Planned Topdown Budget Constraint Staking
autofit | Description |  | Pole staking is a safe and affordable alternative program to defer full pole replacement, which manages the risk of pole failures and provides an alternative to traditional pole replacements. Staking an impaired wood pole that is suitable for the staking method, restores the pole safety and defers full capital cost of pole replacement whilst the transition to alternative pole types is fully implemented. this option is similar to option 1, but with reduced volumes to meet business requirement for reduced capital expenditure across the asset portfolio.
autofit | Alternative Status |  | Candidate
autofit | Alternative Start Date |  | 4547400%
| Reason for selection/rejection |  | This option was rejected after portfolio optimisation to assess risk and expenditure across the whole asset portfolio. It has the lowest NPV and does not manage risk effectively compared to the other options.
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
| Option 4 Planned Topdown Budget Constraint Staking |  | Capex |  |  | 740000 | 740000 | 740000 | 740000 | 740000 | 3700000 | 16590000 | 1624966812.41
|  |  | Opex |  |  | 50000 | 50000 | 50000 | 50000 | 50000 | 250000
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | UARM - Environment and Community - Fire Risk |  |  | 17334.7348 | 1.05%
[9 empty] | UARM - Safety & People - Worker |  |  | 9157.3811 | 0.56%
[9 empty] | UARM - Network Performance Risk |  |  | 1484410.0259 | 90.03%
[9 empty] | UARM - Environment and Community - Other Risk |  |  | 20241.581 | 1.23%
[9 empty] | UARM - Financial Risk |  |  | 72910.1747 | 4.42%
[9 empty] | UARM - Safety & People - Public |  |  | 27528.5501 | 1.67%
[9 empty] | Terminal Value |  |  | 5284.0034 | 0.32%
[9 empty] | Total Investment Cost |  |  | -11899.6387 | 0.72%
[9 empty] | Total |  |  | 1624966.8124
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE | Investment Cost | CAPEX Cost |  | Outcome | 2024 | 0 | Dollar | 740000 | 740000 | 740000 | 740000 | 740000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE | Investment Cost | OPEX Cost |  | Outcome | 2024 | 0 | Dollar | 50000 | 50000 | 50000 | 50000 | 50000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE | Investment Cost | Total Investment Cost |  | Outcome | 2024 | -11899.6387 | Dollar | 790000 | 790000 | 790000 | 790000 | 790000
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE | Terminal Value | Terminal Value |  | Outcome | 2048 | 5284.0034 | Dollar | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Baseline |  | 0 | Dollar | 3367661.75 | 3695667 | 4041690.84 | 4404662.53 | 4783138.17
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE | UARM - PA to Investment | UARM - Environment and Community - Fire Risk |  | Outcome | 2024 | 17334.7348 | Dollar | 3268811.82 | 3494912.33 | 3727862.2 | 3971279.24 | 4216156.19
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Baseline |  | 0 | Dollar | 1779027.05 | 1952301.64 | 2135094.87 | 2326841.09 | 2526777.57
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE | UARM - PA to Investment | UARM - Safety & People - Worker |  | Outcome | 2024 | 9157.3811 | Dollar | 1726807.81 | 1846249.42 | 1969309.32 | 2097898.69 | 2227259.28
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE | UARM - PA to Investment | UARM - Network Performance Risk |  | Baseline |  | 0 | Dollar | 288380001.86 | 316467785.42 | 346098539.02 | 377180572.07 | 409590242.42
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE | UARM - PA to Investment | UARM - Network Performance Risk |  | Outcome | 2024 | 1484410.0259 | Dollar | 279915272.61 | 299276737.9 | 319224728.14 | 340069044.41 | 361038375.5
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Baseline |  | 0 | Dollar | 3932381.93 | 4315390.08 | 4719438.35 | 5143276.43 | 5585218.31
| UARM - PA to Investment | UARM - Environment and Community - Other Risk |  | Outcome | 2024 | 20241.581 | Dollar | 3816955.94 | 4080971.04 | 4352984.06 | 4637219.49 | 4923159.63
| UARM - PA to Investment | UARM - Financial Risk |  | Baseline |  | 0 | Dollar | 14164439.71 | 15544035.08 | 16999416.94 | 18526081.69 | 20117956.36
| UARM - PA to Investment | UARM - Financial Risk |  | Outcome | 2024 | 72910.1747 | Dollar | 13748675.28 | 14699657.68 | 15679448.6 | 16703264.6 | 17733220.99
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE | UARM - PA to Investment | UARM - Safety & People - Public |  | Baseline |  | 0 | Dollar | 5348039.42 | 5868930.51 | 6418436.16 | 6994855.94 | 7595896.91
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE | UARM - PA to Investment | UARM - Safety & People - Public |  | Outcome | 2024 | 27528.5501 | Dollar | 5191060.07 | 5550120.61 | 5920058.33 | 6306618.5 | 6695497.1
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 316971551.72 | 347844109.73 | 380412616.18 | 414576289.75 | 450199229.74
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 307667583.53 | 328948648.98 | 350874390.65 | 373785324.93 | 396833668.69
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 5 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## Option 6 (hidden)
alternative
| Investment Evaluation Summary |  |  |  |  | Investment Code |  | Report Start Year |  | Number of Years | Base Fiscal Year | Currency Scale
[6 empty] | PRJ000500 |  | 2025 |  | 25 | FY23 | Literal
[6 empty] | Investment Name | [5 empty] | Scenario
[6 empty] | R24_D_OH_RESTK _Pole staking | [5 empty] | Approved
autofit | Value Function |  | TasNetworks Value Function |  |  | Version |  | 0.1 |  | Date |  | 2022-10-31
Alternative Overview
75679 | Alternative Name
autofit | Description
autofit | Alternative Status
autofit | Alternative Start Date
Reason for selection/rejection
Alternative Spend Profile and Alternative Value
| Name |  | Account Type |  |  | 2025 | 2026 | 2027 | 2028 | 2029 | R24 Expenditure | Total Expenditure | NPV
0
0
[9 empty] | Value Function Measure |  |  | Value | Value in %
[9 empty] | Total |  |  | 0
Alternative Value Details
| Value Model | Value Measure |  | Type | Impact Year | Value | Unit | 2025 | 2026 | 2027 | 2028 | 2029
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostCAPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostOPEX CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacInvestment CostInvestment CostTotal Investment CostFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacTerminal ValueTerminal ValueTerminal ValueFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Fire RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - WorkerFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Network Performance RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Environment and Community - Other RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskTRUE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Financial RiskFALSE
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicTRUE | [6 empty] | Baseline | 0 | 0 | 0 | 0 | 0
75679PRJ000652 / R24_D_OH_REPOL_Basic Fleet Pole ReplacUARM - PA to InvestmentUARM - PA to InvestmentUARM - Safety & People - PublicFALSE | [6 empty] | Outcome | 0 | 0 | 0 | 0 | 0
Note: Based on the characteristics of the value model, Financial Benefits & Costs was excluded from the chart above - please refer to the "Economic Analysis" sheet for the full breakdown of Investment Value.

## TextFormatting (hidden)
Index | 8
Column Width | 238
Font | Calibri
Font Size | 11
Font Colour
Text | Sheet | Group | Field | Row Height | Row Number
Pole staking is a safe and affordable alternative option to pole replacement, which manages the risk of pole failures. Staking an impaired wood pole restores pole safety and defers full pole replacement for approximately 10 to 15 years. | Investment Summary | Header | Description | 30 | 9
TasNetworks has approximately 240,000 support structures installed on the distribution network to provide support, insulation and adequate clearances between live electrical and the ground, vegetation and building infrastructure. Wood poles deteriorate at a greater rate below or near the ground line compared to higher above the ground, primarily because of greater water availability for biological wood rot growth. Thus, the above ground section may have many more years of useful service remaining when the below ground section has deteriorated. Stakes (or ground-line reinforcing) may be installed on wood poles to strengthen the pole at and below ground level. Staking wood poles commenced in 2002 and the current staked wood pole population is approximately 29,000 poles. Wood poles are generally staked at 30-45 years of age with the staking process typically extending the life of a wood pole by a further 10-15 years. Staking wood poles has proven to be a cost-effective way of ensuring the service life of 40-50 years is attained. | Investment Summary | 0.1 Overview | Background | 165 | 16
Analysis of the performance of the wood pole population has confirmed that performance has not materially deteriorated. Notwithstanding the reasonable performance levels realised to date, additional investment will be required in future years to sustain the performance of the wood pole population and to ensure the number of poles at or exceeding their service life remains manageable. In particular, a plan is required to extend the service life of class S3 wood poles whilst completing the transition to alternative bushfire resistant poles, such as Fibreglass Reinforced Composite (FRC) poles (i.e.: Titan poles) due to an increasing shortage of class S3 wood poles. | Investment Summary | 0.1 Overview | Problem Definition | 90 | 17
TasNetworks has a customer and stakeholder engagement strategy to inform the existing program of work and the upcoming revenue submission. The feedback obtained informs the approach taken by TasNetworks to align our investments with customer needs and impacts. Customer needs addressed by this investment include: - affordability; - supply reliability and safety of the current network; - resilience to future impacts including climate change; and - investment in future networks to unlock community benefits in renewable energy products and services. | Investment Summary | 02. Customer Needs and Impact | Customer Needs and impact | 135 | 18
Performance Measure: Significant incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. Performance Measure: Reportable incidents Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. | Objectives and Analysis | 03. Business Performance Objectives | Safety and Wellbeing | 135 | 17
Performance Measure: Customer net promoter score Investment impact on performance: Replacement of poles reduces the risk of a pole failure resulting in bushfire starts and injury. | Objectives and Analysis | 03. Business Performance Objectives | Our Customers | 60 | 18
Performance Measure: Employee engagement Investment impact on performance: Maintain our vision of ‘powering a bright future.’ | Objectives and Analysis | 03. Business Performance Objectives | Our People | 45 | 19
Performance Measure: Capital expenditure Investment impact on performance: Replacement reduces our total cost when compared to managing end of life pole failures. Performance Measure: Operational expenditure Investment impact on performance: Replacement reduces our operational cost in replacing poles in poor condition in a planned way prior to failure. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Sustained Cost Management | 135 | 20
Performance Measure: Service incentive bonuses earned - distribution. Investment impact on performance: Replacement of poles will reduce the risk of failure and therefore minimise prolonged outages. | Objectives and Analysis | 03. Business Performance Objectives | Our Business - Network Service | 60 | 21
Employee impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. | Objectives and Analysis | 04. Business Risks | Death or Injury (Employee) | 15 | 23
Public impacted by pole or contacts live conductors directly or indirectly after they fall to ground following pole failure. | Objectives and Analysis | 04. Business Risks | Death or Injury (Public) | 15 | 24
If a sustainable proactive program is not implemented, increased failure rates will result in a large increase in the program of work and ultimately increase power price to customer. | Objectives and Analysis | 04. Business Risks | Sustainable and Predictable Pricing | 30 | 25
An average of 10 unassisted pole failures occur per year currently. | Objectives and Analysis | 04. Business Risks | Widespread Power Disruption | 15 | 26
TasNetworks has recorded ground fire starts from pole failures. | Objectives and Analysis | 04. Business Risks | Bushfire Start | 15 | 27
| Objectives and Analysis | 04. Business Risks | Loss of Major Industrial | 15 | 28
Customers have an expectation of consistent and reliable power supply which these assets provide. | Objectives and Analysis | 04. Business Risks | Customer Focus | 15 | 29
| Objectives and Analysis | 04. Business Risks | Business Continuity Management | 15 | 30
| Objectives and Analysis | 04. Business Risks | Cyber Security | 15 | 31
| Objectives and Analysis | 04. Business Risks | Private Assets | 15 | 32
| Objectives and Analysis | 04. Business Risks | Energy Policy and Regulation | 15 | 33
| Objectives and Analysis | 04. Business Risks | Project Marinus (D&A) | 15 | 34
| Objectives and Analysis | 04. Business Risks | Tasmanian Power System Complexity | 15 | 35
| Objectives and Analysis | 04. Business Risks | Emerging Complexity of the NEM | 15 | 36
The strategic objective is to manage the risk to customers by developing a risk based strategic plan. This includes a condition/risk-based approach to manage the assets to maintain reliability and security of the network and effectively manage the safety and bushfire risk associated with maintaining the asset. | Objectives and Analysis | 05. Strategic Objectives | Strategic Objectives | 45 | 38
Towards 2030 We continually assess what value means to our customers to better serve all our stakeholders: Ensuring our electricity network remains resilient and fit-for-purpose by proactively maintaining assets, designing out risks, and making prudent investments of long-term value: The long-term impact of asset maintenance and renewal has been reviewed out to 2050. The analysis clearly demonstrates work should be done to mitigate risks to customers now and into the future. To ensure our capital is used wisely, we will streamline our investment planning to achieve optimised investment strategies and have the best delivery model: Investment planning has been developed to align all asset categories. The plan has been developed out to 2050 to ensure the long-term objectives of optimising investment strategies is achieved. | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #1 | 165 | 39
TasNetworks Business Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #2 | 15 | 40
Bushfire Risk Mitigation Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #3 | 15 | 41
Overhead Line Support Structures Asset Management Plan | Objectives and Analysis | 05. Strategic Objectives | Strategic Document #4 | 15 | 42
| Objectives and Analysis | 05. Strategic Objectives | Strategic Document #5 | 15 | 43
The objective of this project is to implement a safe and affordable program that manages the risk of pole failures and provides an alternative to traditional pole replacements. Staking impaired wood poles that are suitable for staking restores pole safety and defers full capital cost of pole replacement for 10 to 15 years. With increasing shortage of class S3 wood poles, a plan is required to extend the service life of class S3 wood poles whilst completing the transition to alternative bushfire resistant poles (currently FRC Titans). | Objectives and Analysis | 06. Project Objectives | Project Objectives | 90 | 44
Western Power Wood Poles Audit (2013), Report2013_17-Western-Power-Wood-Poles.pdf (audit.wa.gov.au). ESV Pole Inspection Audit of Powercor (2019). ESV investigation requires safety improvements for Powercor pole regime – Energy Safe Victoria. | Objectives and Analysis | 07. Options Analysis | Benchmarking | 75 | 45
Expert analysis is used to design and assess the condition of wood poles. These findings are then used to develop TasNetworks asset management strategies. Examples of these resources are: - Australian Standard for Design of Overhead Lines AS/NZS 7000 - 2016; - SAA HB 331:2020 Overhead Design Manual ; - Economic Evaluation of Treated Wooden Pole Inspection Cycles (R295189); - Network Policy NN R AM 11 Wood pole reinstatement by ground-line reinforcement (NW10149727); - ENA DOC 015-2006 National Guidelines for Prevention of Unauthorised Access to Electricity Infrastructure; - Nathan Spencer, Leith Elder, Pole Service Life - An analysis of Country Energy Data , White Paper it is published accessible on http://www.koppers.com.au/Utility-Poles/default.aspx; - Timber – Natural Durability Ratings AS 5604 – 2005; - UTAS Final Report Identification of soft rot decay fungi in eucalypt power pole samples( R 719238); and - Energy Network Association (ENA) Pole Fire Test. | Objectives and Analysis | 07. Options Analysis | Expert Findings | 180 | 46
The program will continue for the whole regulatory period and beyond to manage and flatten forecast pole replacement volumes to a manageable level. | Objectives and Analysis | 08. Investment Timing | Investment Timing | 30 | 47
The benefits to TasNetworks from implementation of the recommended option will be: - longer asset service life for wood poles; - reduced capital expenditure required to maintain wood pole fleet (with resulting reduced average unit rate for RIN benchmarking); - maintain unassisted and assisted pole failure rates; and - staked wood poles remain vulnerable to bushfire risks. | Objectives and Analysis | 09. Expected Outcomes and Benefits | Expected Outcomes and Benefits | 90 | 48
Staking extends pole service life by 10-15 years. FRC /Titan pole service life expectancy is 65 years (from supplier Dulhunty Engineering). The service life expectation of plantation grown timber, will be no better than a local native species class S4, based on observed short service life of similar class S2 species imported from intestate. | Objectives and Analysis | 10. Assumptions | Assumptions | 90 | 49
A RIT-D is not required because this is a high volume, low cost, program with separate sites identified where assets have failed a serviceability test by asset inspection and this program is an alternative to full asset replacement. | Objectives and Analysis | 11. Regulatory Considerations | Regulatory Investment Test | 30 | 50
No | Objectives and Analysis | 11. Regulatory Considerations | Meet or manage the expected demand for Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 51
Yes | Objectives and Analysis | 11. Regulatory Considerations | Comply with all applicable regulatory obligations associated with the provision of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 52
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the quality, reliability and security of supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 53
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the reliability and security of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 54
Yes | Objectives and Analysis | 11. Regulatory Considerations | Maintain the safety of the system through the supply of Standard Control Services (Distribution)/Prescribed Services (Transmission). | 15 | 55
Option 1 (Planned Stake impaired wood pole condition based) is recommended for approval as it best satisfies the customer and business needs. | Objectives and Analysis | 12. Recommendation | Recommendation | 30 | 56
Pole staking is a safe and affordable alternative program to defer full pole replacement, which manages the risk of pole failures and provides an alternative to traditional pole replacements. Staking an impaired wood pole that is suitable for the staking method, restores the pole safety and defers full capital cost of pole replacement whilst the transition to alternative pole types is fully implemented. | Option 1 | Description |  | 30
This option has been selected as it has a similar NPV value compared to pole replacement options with a significantly lower capital expenditure. This option effectively manages the risk of unassisted pole failure, maintains network reliability and reduces the lifecycle costs of distribution support structures. | Option 1 | Reason for selection/rejection |  | 30
This option ceases the pole staking program and increases pole replacement volumes with class S4 wood poles. | Option 2 | Description |  | 15
This option is rejected due to significant increase in capital expenditure and does not meet the business nor customer needs to manage affordability. | Option 2 | Reason for selection/rejection |  | 15
This option ceases the pole staking program and increases pole replacement volumes with titan FRC poles for increased bushfire resilience. | Option 3 | Description |  | 15
This option is rejected due to significant increase in capital expenditure and does not meet the business nor customer needs to manage affordability. Portfolio optimisation identified that the increased bushfire resilience provided by the use of Titan FRC poles is outweighed by the increased cost of pole replacements. | Option 3 | Reason for selection/rejection |  | 30
Pole staking is a safe and affordable alternative program to defer full pole replacement, which manages the risk of pole failures and provides an alternative to traditional pole replacements. Staking an impaired wood pole that is suitable for the staking method, restores the pole safety and defers full capital cost of pole replacement whilst the transition to alternative pole types is fully implemented. this option is similar to option 1, but with reduced volumes to meet business requirement for reduced capital expenditure across the asset portfolio. | Option 4 | Description |  | 30
This option was rejected after portfolio optimisation to assess risk and expenditure across the whole asset portfolio. It has the lowest NPV and does not manage risk effectively compared to the other options. | Option 4 | Reason for selection/rejection |  | 15
| Option 5 | Description
| Option 5 | Reason for selection/rejection
| Option 6 | Description
| Option 6 | Reason for selection/rejection