network service provider

DISTRIBUTION LOSS FACTOR

MORANBAH north coal nsp

AUSTRALIAN ENERGY REGULATOR

FINANCIAL YEAR 2011-12

Document History and Status

| Revision | Date issued | Reviewed | Approved | Date approved | Revision type |
| --- | --- | --- | --- | --- | --- |

| Project Number | : | MNC 3262 |
| --- | --- | --- |
| Name of Project | : | NSP obligations variable pricing 2011/12 |
| Report | : | input.doc |
| Author | : |  |
| Project Manager | : |  |
| Document Version | : | 1.0 |
| Report Status | : | Issue for Audit |
| Last Revised | : |  |

TABLE OF CONTENTS

1.	Summary	1

2.	METHODOLOGY AND CALCULATIONS	2

2.1	Metered Data - Generation and Connection Point	2

2.1.1	Generation and Load Projection for 2011/12	3

2.1.2	Network Connection Points	3

2.1.3	Methodology	4

2.1.4	Distribution Loss Factor	5

3.	appendix 1 – SCHEMATIC OF moranbah north COAl mine nsp	6

4.	appendix 2- additional authorized demand (extracts of the connection application)	7

5.	appendix 3 – report ncm17699	8

# Summary

The terms of Hill Michael’s engagement with Moranbah North Coal Network Service Provider (MNCNSP) include calculation of distribution loss factors in accordance with Section 3.6.3 (i) of the National Electricity Rules (NER). An extract of the relevant clause from the current version (Version 41) of the NER is given below:

“Each year the Distribution Network Service Provider must determine the distribution loss factors to apply in the next financial year in accordance with clause 3.6.3(g) and provide these to AEMO for publication by 1 April. Before providing the distribution loss factors to AEMO for publication, the Distribution Network Service Provider must obtain the approval of the AER for the distribution loss factors it has determined for the next financial year.”

Hill Michael has calculated the distribution loss factors based on the metered data for 2010 and the proposed generation for the financial 2011-12. The embedded generation is dependent on the mine for fuel (coal seam methane gas), therefore, changes to the production level of the mine will impact the generation output.

The site specific DLF calculated using a Marginal Loss Factor (MLF) approach is 0.9888 for the EDL embedded generation connected to the Moranbah North Coal Mine NSP. This distribution loss factor has been calculated in accordance with the methodology approved by the QCA as described in Report NCM 17699 Determination of Distribution Loss Factors for Embedded/Local Generators.

In addition to the NER obligations, as required by the Australian Energy Regulator, this report has been provided to IES (Intelligent Energy Systems) for independent positive certification. Additional supporting evidence has been provided to IES to enable independent verification of calculations.

SIGNED, on the 11th day of March 2011

| Nalika Gamage | Soruby Bharathy MIEAust (CPEng) |
| --- | --- |
| Consulting Engineer | Senior Consulting Engineer |

# METHODOLOGY AND CALCULATIONS

## Metered Data - Generation and Connection Point

The reconciled metered data for the parent meter and the revenue meter at the generator (National Metering Identifiers are given below) have been obtained from the authorised Metering Provider.

| Parent NMI | QDDD000005 |
| --- | --- |
| TNI / MDA | MRN / Ergon Energy |
| Generator NMI | 7102000038 |

Below is the summary of the data based on the most recent half hourly metered data available for a consecutive 12 month period at the time of determining loss factors. The mine load is estimated based on the difference between the connection point and the generation metered data.

- Connection Point (MWh): This is the total energy from connection point meter.

Net negative energy indicates that the energy provided by generation is higher than the energy consumed by the load for that month. The converse is true for Net positive energy.

- Generation (MWh): This is the monthly energy output of the generator measured at the generator revenue meter.

Net negative energy indicates the energy provided by the generators to the system

- Estimated Mine Load (MW): Difference of Connection Point (MWh) and Generation (MWh) converted to MW. The conversion between MWh to MW is calculated based on 24 hours a day operation of the mine.

| Date | Connection Point (MWh) | Generation (MWh) | Estimated Mine Load (MW) |
| --- | --- | --- | --- |
| Jan-10 | -18,195.33 | -27,782.97 | 12.89 |
| Feb-10 | -13,566.45 | -22,620.52 | 13.47 |
| Mar-10 | -13,617.72 | -24,786.79 | 15.01 |
| Apr-10 | -13,473.99 | -23,548.61 | 13.99 |
| May-10 | -14,900.18 | -25,378.38 | 14.08 |
| Jun-10 | -13,436.13 | -23,367.43 | 13.79 |
| Jul-10 | -14,655.69 | -24,757.72 | 13.58 |
| Aug-10 | -13,551.15 | -23,248.27 | 13.03 |
| Sep-10 | -13,370.42 | -23,460.91 | 14.01 |
| Oct-10 | -12,677.33 | -25,280.87 | 16.94 |
| Nov-10 | -14,764.04 | -25,049.75 | 14.29 |
| Dec-10 | -6,849.60 | -16,521.52 | 13.00 |

Table 1: Metered Data for 2010

### Generation and Load Projection for 2011/12

Generation Projection: 	EDL Power Station advises a 36 MW of installed capacity at unity power factor will be available in 2011/12. This availability takes into account contingencies and planned outages.

Mine Load Projection: 	Moranbah North Coal Mine load is assumed based on the available historical data in 2010. MNCM advises that the mine load PF will be increased from 0.7 to 0.95 from January 2012.

Table 2 below shows the generation forecast of EDL power station and mine loads.

| Date | Generation (kW) | Generation (MWh) | Mine Load (kW) | Mine Load pf | Mine Load (MVA) |
| --- | --- | --- | --- | --- | --- |
| Jul-11 | 36,000 | 26,784 | 13.58 | 0.70 | 19.40 |
| Aug-11 | 36,000 | 26,784 | 13.03 | 0.70 | 18.62 |
| Sep-11 | 36,000 | 25,920 | 14.01 | 0.70 | 20.02 |
| Oct-11 | 36,000 | 26,784 | 16.94 | 0.70 | 24.20 |
| Nov-11 | 36,000 | 25,920 | 14.29 | 0.70 | 20.41 |
| Dec-11 | 36,000 | 26,784 | 13.00 | 0.70 | 18.57 |
| Jan-12 | 36,000 | 26,784 | 12.89 | 0.95 | 13.56 |
| Feb-12 | 36,000 | 24,192 | 13.47 | 0.95 | 14.18 |
| Mar-12 | 36,000 | 26,784 | 15.01 | 0.95 | 15.80 |
| Apr-12 | 36,000 | 25,920 | 13.99 | 0.95 | 14.73 |
| May-12 | 36,000 | 26,784 | 14.08 | 0.95 | 14.82 |
| Jun-12 | 36,000 | 25,920 | 13.79 | 0.95 | 14.52 |

Table 2: Forecast Data for 2011-12

Note:

It is planned to increase the authorized demand on the existing MNCNSP connection point   to secure the power supply for the proposed Grosvenor mine project. As per the demand data in Table 3.31 and 3.3.2 (refer appendix 2- additional authorized demand) of the connection application which is already submitted to Ergon Energy, there will be 2.86MW additional load at 0.95 PF in the first quarter of 2012. However, as the connection point of this additional load is not yet confirmed, this load is not included for the 2011/12 DLF calculations.

### Network Connection Points

The Moranbah North Coal Mine Network Service Provider (MNCNSP) owns and operates the 66 kV distribution network which is connected to the Ergon Energy Corporation Limited (EECL) Moranbah substation.

The embedded generation owned and operated by EDL will be the only customer on the MNCNSP network; subsequently MNCNSP will have only one distribution network connection point. The mine is a customer of EECL and the mine distribution network connection point is located at the Moranbah 66 kV busbar. The mine connection point is also the MNCNSP connection point to the EECL network service. The EDL embedded generator distribution network connection point is on the MNCNSP 66 kV network.

Figure 1 below shows the location of the connection points and the network for which losses are calculated.

Figure 1: Simplified Representation of the Network

### Methodology

EDL Generator DLF Calculation

MNCNSP has one connection point on its distribution network and the site specific DLF for this connection point has been calculated in accordance with the methodology approved by the Queensland Competition Authority (QCA) as described in Report NCM 17699 Determination of Distribution Loss Factors for Embedded/Local Generators. (Refer appendix 3 – report ncm17699)

The DLF is a static loss factor which is applied to the embedded generator distribution network connection point for the full financial year. The steps undertaken to calculate the DLF are summarised below.

- Request expected mine consumption and embedded generation forecasts for the 2011-12 financial year.

- Prepare and review the network model for the MNCNSP distribution network by incorporating any proposed changes to the network occurring in the period leading up to the financial year for which the embedded generator DLF is being calculated.

The PSS/SINCAL network model (given in Figure 2) represents the following:

  - Moranbah (MRN) 66 kV connection point as an infinite bus;

  - Moranbah North Mine load at the 66 kV busbar at the Mine Boundary Substation;

  - EDL Generation Tee off to MNCNSP at the generator connection point.

- Using the Network Model and Load Flow Analysis, the following steps are performed.

    - Note the loss on the NSP network for initial generation (A). The NSP network is between the 66kV MNCNSP connection point at Moranbah Substation and Moranbah North Coal Mine connection point.

    - Increment the generation by 1 MW and note the new loss on the NSP Network (B).

    - Run a set of load flow studies for each month of the next financial year using the forecast mine load and embedded generation data.

    - The loss due to the increment in generation per MW is calculated               (B-A)/1000.

- Calculate the MLF and DLF in accordance with the methodology approved by the QCA as described in Report NCM 17699.

### Distribution Loss Factor

The loss under proposed generation on the NSP network is noted (A), then the generation is incremented by 1 MW and the new loss on the NSP network is observed (B). The difference in the loss after the 1 MW increment is (B-A)/1000 per MW. The marginal loss factor is 1 less the loss per MW of generation increment.

The volume weighted DLF is weighted on the average forecast generation per month.

| Period | A (kW) NSP Loss | B (kW) NSP Loss for Increment in Generation | MLF [1 - (B-A)/1000] | DLF [SQRT (MLF)] |
| --- | --- | --- | --- | --- |
| Jul-11 | 360 | 382 | 0.9776 | 0.9887 |
| Aug-11 | 363 | 387 | 0.9760 | 0.9879 |
| Sep-11 | 358 | 380 | 0.9779 | 0.9889 |
| Oct-11 | 355 | 374 | 0.9806 | 0.9903 |
| Nov-11 | 357 | 379 | 0.9782 | 0.9891 |
| Dec-11 | 363 | 387 | 0.9761 | 0.9880 |
| Jan-12 | 275 | 298 | 0.9766 | 0.9882 |
| Feb-12 | 264 | 287 | 0.9771 | 0.9885 |
| Mar-12 | 235 | 256 | 0.9795 | 0.9897 |
| Apr-12 | 254 | 276 | 0.9776 | 0.9887 |
| May-12 | 252 | 274 | 0.9776 | 0.9888 |
| Jun-12 | 258 | 280 | 0.9774 | 0.9886 |
|  | Volume Weighted Average DLF |  |  | 0.9888 |

Table 3: Volume Weighted Average DLF

# appendix 1 – SCHEMATIC OF moranbah north COAL NSP

Figure 2: Moranbah North Coal NSP Network as modelled in PSS/SINCAL

# appendix 2- additional authorized demand (extracts of the connection application)

# appendix 3 – report ncm17699