8th March 2011

Mr Chris Pattas

General Manager

Australian Energy Regulator

GPO Box 520

Melbourne VIC  3001

Dear Sir,

Re: OneSteel Limited Exempt Network - Application for

Approval of Distribution Loss Factors on OneSteel’s Mayfield site.

This letter seeks approval from AER to update the 11kV DLF for Donhad Pty Ltd NMI 7102000008, Hunter Development Corporation NMI 7102000009,  Koppers NMI 7102000010 and Theiss (acting for BHPBilliton) NMI 7102000011.

The new DLF is;

- 11kV DLF =  1.02031

If you have any queries in relation to this request, please phone Gary Elsley on 02 49354910

Yours sincerely,

Peter Hansen

General Manager – Commercial

OneSteel network DLF calculations for 11kV Sites

| OneSteel 11KV network DLF calculation |  |  | 2011- 2012 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| date | OneSteel 11KV @ NMI | OneSteel 11KV consumer site metered | DLF |  | monthly metered adjusted by set DLF |  |
| Jan-10 | 8668248.41 | 8358411.065 | 1.0371 |  | 8528145.563 |  |
| Feb-10 | 11355688.25 | 11131674.62 | 1.0201 |  | 11357725.86 |  |
| Mar-10 | 14288569.25 | 14103777.54 | 1.0131 |  | 14390183.36 |  |
| Apr-10 | 11148972.49 | 11115805.76 | 1.0030 |  | 11341534.75 |  |
| May-10 | 11136502.04 | 10835704.96 | 1.0278 |  | 11055745.93 |  |
| Jun-10 | 11451133.59 | 11262994.81 | 1.0167 |  | 11491712.77 |  |
| Jul-10 | 13444781.67 | 13109264.74 | 1.0256 |  | 13375474.96 |  |
| Aug-10 | 13148507.54 | 12876710.86 | 1.0211 |  | 13138198.6 |  |
| Sep-10 | 13386938.55 | 13110520.66 | 1.0211 |  | 13376756.38 |  |
| Oct-10 | 10661951.05 | 10389216.38 | 1.0263 |  | 10600190.5 |  |
| Nov-10 | 8442528.877 | 8355803.857 | 1.0104 |  | 8525485.41 |  |
| Dec-10 | 10880201.69 | 10617264.2 | 1.0248 |  | 10832869.3 |  |
|  | 138014023.4 | 135267149.4 | 1.02031 |  | 138014023.4 |  |
|  | Note - OneSteel includes all internal consumers, Donhad, Koppers, HDC, Thiess |  |  |  |  |  |
|  | The Distribution Loss Factor DLF is calculated from the sum of the 12 monthly kWhs metered at the NMI, divided by the sum of the OneSteel consumer site metered KWh. |  |  |  |  |  |

ASSESSMENT OF DLFS

In determining the DLF, the following points have been considered;

• DNSPs must assign customers to the appropriate DLF categories based on their connection characteristics;

Comply with clause 3.6.3 – connections are at 11KV

• DNSPs must identify the appropriate generators and consumers who require site-specific DLFs and determine their site-specific DLFs based on the required data;

Not Applicable

• DNSPs must undertake a reconciliation between the actual and forecast losses in the previous financial year;

Comply with clause 3.6.3 – see tables attached

• DNSPs must use the most recent actual load and generation data available for a consecutive 12 month period but may adjust this data by projected load growth in the financial year in which the proposed DLFs are to apply.

Comply with clause 3.6.3 (see note 1)

• The levels of losses are consistent with that of a well managed network;

Comply with clause 3.6.3

• DNSPs ‘ calculation methodologies are uniform and consistent with the methodologies used previously;

Comply with clause 3.6.3

• DNSPs have made appropriate allowance for theft and metering inaccuracy.

Comply with clause 3.6.3

Note

Projected load increases have been assessed. Hunter Development Corporation and the NSW Government have undisclosed plans in the future, to redevelop the site. At that time the load may increase.