## 33kV Load Losses

### This is an example of demonstrating losses for a particular 33kV load, namely the Delta EMD plant – NMI 7102000007.

### Losses are shown on a monthly basis.

### No Load Losses

No load losses for transformers are 72kW per transformer.

There are 2 transformers in parallel, so total no load losses are 144kW.

Proportion of EMDs contribution to these losses is simply the ratio of EMD's load to the Total Load,

So

EMDLoad = 5000;	% EMDLoad is typically 5000 MWh for a month

TotalLoad = 21000;	% The total load is typically 21,000 MWh for a month

NoLoadLosses = EMDLoad/TotalLoad * 144e3  	% Watts

NoLoadLosses =

3.4286e+004

### Copper Losses

Load losses are 728 kW at 120 MW load.

The current at this load is …

Current = 120e6 / 33e3 / sqrt(3)  	% Amps

Current =

2.0995e+003

With load losses of 728 kW, the effective resistance is …

EffRes = 728e3/Current^2   % Ohms

EffRes =

0.1652

For a typical load of 5000 MWh for a month the equivalent average instantaneous power is …

PowerAv = EMDLoad / 24 / 30  	% MW, where there are 24 hours in a day and an average of 30 days in a month

PowerAv =

6.9444

The average current can then be found to be …

AvCurrent = PowerAv * 1e6 / sqrt(3) / 33e3  	%  Amps

AvCurrent =

121.4963

So the total copper losses are …

CuLosses = AvCurrent ^2 * EffRes  	% Watts

CuLosses =

2.4381e+003

### Total Losses

The total losses are therefore ….

TotalLosses = NoLoadLosses + CuLosses 		% Watts

TotalLosses =

3.6724e+004

Over a period of a month the total Watt-hour losses are …

TotalWhLosses = TotalLosses * 24 * 30  	% Wh

TotalWhLosses =

2.6441e+007

Therefore the Loss Factor is ….

LF = TotalWhLosses / EMDLoad / 1e6

LF =

0.0053