## Augmentation
Original Proposal Data $000 nominal
Proposed Expenditure ($,000 nom)
|  |  | Unique | Network | Responsible | RIN Tab | Plan | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26
Category / Description |  |  | Identifier | Manager | Person |  | Reference | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Jun | Jul-Dec |  | Sub-Trans | Zone S/Stn | HV Feeder | Dist T/F | LV Feeder | Not Aug
Capacity
Upgrade
| Moderate load growth forecast | Connection Point Capacity | 1 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 21118.6435 | 9782.121 | 5304.7795 | 2054.1365 | 1042.258 | 336.7295 | 705 | 4945 | 6005 | 1765 | 0 | 0 | 0 |  | 75% |  |  |  |  | 25%
|  | Connection Point Capacity - New | 2 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% |  |  |  |  | 0%
|  | LV & Distribution Transformers (QoS BAU) | 3 | Planning | P Driver | AUGEX | AMP.1.1.01 | 8567.648 | 8048.0985 | 7990.0455 | 7927.6765 | 7594.398 | 7414.9675 | 8390 | 9000 | 9400 | 9800 | 10200 | 10600 | 10800 |  |  |  |  | 60% | 15% | 25%
|  | Distribution Feeders | 4 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 2753.692 | 2830.1435 | 538.5155 | 852.8156 | 753.1906 | 17.6415 | 2420 | 2750 | 330 | 85 | 625 | 905 | 730 |  |  |  | 100% |  |  | 0%
|  | NER Compliance (Pwr Factor) | 5 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100% |  |  |  | 0%
|  | Strategic Network Capacity (Other) | 6 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 | 4100 |  |  | 50% | 15% |  | 10% | 25%
|  | Substation Capacity | 7 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 22979.3624 | 21985.8134 | 22031.279 | 18601.732 | 14024.4059 | 8643.1649 | 6457.925 | 3575 | 2440 | 3320 | 2405 | 800 | 600 |  |  | 100% |  |  |  | 0%
|  | Substation Capacity - New | 8 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 100% |  |  |  | 0%
|  | Subtransmission Network - Country | 9 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100% |  |  |  |  | 0%
|  | Subtransmission Network | 10 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 16619.399 | 10138.246 | 3975.9815 | 6064.6535 | 6915.278 | 7769.0115 | 9410 | 8720 | 4725 | 1140 | 1595 | 5570 | 9090 |  | 80% |  |  |  |  | 20%
|  | Distribution Line - SWER Replacements | 11 |  |  |  |  | 641.018 | 823.758 | 361.389 | 103.3525 | 44.4252 | 123.6387 | 445 | 700 | 700 | 700 | 700 | 700 | 700 |  |  |  | 30% | 15% | 15% | 40%
|  | Voltage Regulation | 12 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 1025 | 2855 | 2855 | 2855 | 3660 | 3660 | 3660 |  |  |  | 25% | 25% |  | 50%
|  | Land | 13 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1550 | 1550 | 0 |  |  | 100% |  |  |  | 0%
|  | LV Two Way Network (QoS) | 14 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 1250 | 1250 | 0 | 2000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 |  |  |  | 20% | 20% | 20% | 40%
|  | Supply Security (KI) | 15 | Planning | S Fraser | AUGEX | AMP.1.1.01 | 0 | 0 | 0 | 4815.9945 | 13341.887 | 8525.8925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 35% |  | 15% |  |  | 50%
|  | Substation Standards Digital Optimisation | 16 |  |  | AUGEX
17
|  | Flexible load management | 18 |  |  | AUGEX
19
20
21
22
23
24
25
26
27
28
29
30
|  | Upgrade |  |  |  |  | subtotal | 76779.7629 | 57708.1804 | 44301.99 | 45770.361 | 49065.8427 | 36931.0461 | 34952.925 | 40645 | 34555 | 27765 | 28835 | 31885 | 33680
|  | Sub-Trans | [5 empty] | 29134.5018 | 15447.1876 | 7159.3698 | 8077.9232 | 10983.5763 | 9451.8187 | 8056.75 | 10684.75 | 8283.75 | 2235.75 | 1276 | 4456 | 7272
|  | Zone S/Stn | [5 empty] | 25029.3624 | 24035.8134 | 24081.279 | 20651.732 | 16074.4059 | 10693.1649 | 8507.925 | 5625 | 4490 | 5370 | 6005 | 4400 | 2650
|  | HV Feeder | [5 empty] | 3560.9974 | 3692.2709 | 1261.9322 | 2471.2205 | 3632.8012 | 1948.617 | 3824.75 | 5088.75 | 2668.75 | 2423.75 | 3165 | 3445 | 3270
|  | Dist T/F | [5 empty] | 5236.7415 | 4952.4228 | 4848.2356 | 5022.1088 | 4813.3026 | 4467.5263 | 5757 | 7018.75 | 7258.75 | 7498.75 | 7940 | 8180 | 8300
|  | LV Feeder | [5 empty] | 1791.2999 | 1740.7785 | 1662.7152 | 1864.6543 | 1805.8235 | 1540.7909 | 2135.25 | 2665 | 2725 | 2785 | 2845 | 2905 | 2935
[8 empty] | 64752.903 | 49868.4731 | 39013.5318 | 38087.6388 | 37309.9095 | 28101.9178 | 28281.675 | 31082.25 | 25426.25 | 20313.25 | 21231 | 23386 | 24427
|  | Not augmentation $000 nominal | [5 empty] | 12026.8599 | 7839.7073 | 5288.4582 | 7682.7222 | 11755.9332 | 8829.1283 | 6671.25 | 9562.75 | 9128.75 | 7451.75 | 7604 | 8499 | 9253
|  | CPI $ 2020 | [7 empty] | 106.6 | 108.4 | 110 | 112.1 | 114.342 | 117.1662 | 120.0603 | 123.0257 | 126.0645 | 129.1783 | 132.369
|  | CPI Adj $ 2020 | [7 empty] | 1.0726 | 1.0548 | 1.0395 | 1.02 | 1 | 0.9759 | 0.95237 | 0.92942 | 0.90701 | 0.88515 | 0.86381
|  | Sub-Trans | [7 empty] | 7679.3308 | 8520.7186 | 11417.128 | 9640.8551 | 8056.75 | 10427.1982 | 7889.2099 | 2077.9401 | 1157.3474 | 3944.2234 | 6281.6459
|  | Zone S/Stn | [7 empty] | 25830.2214 | 21783.767 | 16708.9065 | 10907.0282 | 8507.925 | 5489.4115 | 4276.1494 | 4990.9599 | 5446.6073 | 3894.655 | 2289.1036
|  | HV Feeder | [7 empty] | 1353.5821 | 2606.6817 | 3776.1977 | 1987.5893 | 3824.75 | 4966.0876 | 2541.6422 | 2252.6702 | 2870.6931 | 3049.3379 | 2824.6675
|  | Dist T/F | [7 empty] | 5200.3467 | 5297.3982 | 5003.2968 | 4556.8768 | 5757 | 6849.5657 | 6913.0288 | 6969.4526 | 7201.6756 | 7240.5178 | 7169.6454
|  | LV Feeder | [7 empty] | 1783.4726 | 1966.8663 | 1877.1043 | 1571.6068 | 2135.25 | 2600.7612 | 2595.2132 | 2588.4215 | 2580.4493 | 2571.3575 | 2535.2903
|  | Augmentation Capex Real $ 2020 000's | [7 empty] | 41846.9536 | 40175.4317 | 38782.6333 | 28663.9562 | 28281.675 | 30333.0243 | 24215.2435 | 18879.4442 | 19256.7728 | 20700.0915 | 21100.3527
|  | Augmentation | [7 empty] | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
|  | Sub-Trans | [7 empty] | 7679330.8117 | 8520718.637 | 11417128.043 | 9640855.0536 | 8056750 | 10427198.2044 | 7889209.9027 | 2077940.1318 | 1157347.3713 | 3944223.362 | 6281645.9239 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816 | 5296260.816
|  | Zone S/Stn | [7 empty] | 25830221.4204 | 21783766.9773 | 16708906.546 | 10907028.2037 | 8507925 | 5489411.5351 | 4276149.3844 | 4990959.8604 | 5446607.339 | 3894655.0253 | 2289103.6439 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647 | 4397814.4647
|  | HV Feeder | [7 empty] | 1353582.0977 | 2606681.6564 | 3776197.7362 | 1987589.3313 | 3824750 | 4966087.6354 | 2541642.2427 | 2252670.1977 | 2870693.1271 | 3049337.8551 | 2824667.5153 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955 | 3084183.0955
|  | Dist T/F | [7 empty] | 5200346.7232 | 5297398.1693 | 5003296.7634 | 4556876.8344 | 5757000 | 6849565.7266 | 6913028.8072 | 6969452.5611 | 7201675.6489 | 7240517.7516 | 7169645.3752 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118 | 7057314.3118
|  | LV Feeder | [7 empty] | 1783472.5942 | 1966866.3071 | 1877104.2611 | 1571606.7519 | 2135250 | 2600761.1984 | 2595213.1565 | 2588421.4546 | 2580449.2722 | 2571357.4656 | 2535290.2622 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349 | 2578582.1349
|  | Augmentation Capex Real $ 2020 | [7 empty] | 41846953.6472 | 40175431.7471 | 38782633.3496 | 28663956.175 | 28281675 | 30333024.2998 | 24215243.4935 | 18879444.2055 | 19256772.7585 | 20700091.4596 | 21100352.7205 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229 | 22414154.8229
|  | Notes | [7 empty] | 41846.9536 2016: 2026/27 to 2039/40 based on the average spend over the 6 year period 2020/21 to 2025/26
LRMC sample shaded

## Replacement
Original Proposal Data $000 nominal
[6 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26
Asset Replace/Refurbish | [19 empty] | Sub-Trans | Zone S/Stn | HV Feeder | Dist T/F | LV Feeder | Not Aug | bar: 2015/16 to 2019/20
Lines
Planned
|  |  |  | REPEX | Historical | 2018/19: 0 | [6 empty] | 100%
|  | Cable Replacement - Planned | 60 | REPEX | AMP.3.1.09 | 1078.8215 | 1094.638 | 918.086 | 2321.4585 | 4054.9275 | 7337.056 | 5979.6164 | 1427.8492 | 1346.4656 | 1346.4656 | 1346.4656 | 1346.4656 | 1346.4656 |  |  |  | 15% |  | 10% | 75%
|  | Conductor Replacement - Planned | 61 | REPEX | AMP.3.1.10 | 2758.806 | 2369.665 | 1850.495 | 3193.04 | 7497.23 | 10194.965 | 6672.1153 | 3170.9458 | 2877.6611 | 2877.6611 | 2877.6611 | 2877.6611 | 2877.6611 |  |  |  | 15% |  | 10% | 75%
|  | Line Ancillary Equipment - Planned (incl LFIs, fences, gates, signs etc) | 62 | REPEX | AMP.3.1.20 | 0 | 0 | 0 | 0 | 0 | 0 | 142.757 | 428.271 | 571.028 | 571.028 | 571.028 | 571.028 | 571.028 | [6 empty] | 100%
|  | Line Regulation - Planned (incl regulators, capacitors) | 63 | REPEX | AMP.3.1.19 | 14.058 | 0 | 0 | 0 | 0 | 0 | 289.1 | 867.3 | 1156.4 | 1156.4 | 1166.4 | 1176.4 | 1176.4 | [6 empty] | 100%
|  | Overhead Line Components - Planned (incl insulators, crossarms, taps, pole earths) | 64 | REPEX | AMP.3.1.06 | 6048.607 | 9507.4325 | 11844.48 | 12109.3675 | 15478.411 | 15464.1805 | 12627.2854 | 13181.8562 | 13459.1416 | 13459.1416 | 13459.1416 | 13459.1416 | 13459.1416 | [6 empty] | 100%
|  | Poles - Planned | 65 | REPEX | AMP.3.1.05 | 19561.4045 | 17708.8755 | 16350.2195 | 16859.1995 | 16405.5355 | 14741.129 | 16715.7243 | 19747.1728 | 21262.8971 | 21262.8971 | 21262.8971 | 21262.8971 | 21262.8971 | [6 empty] | 100%
|  | Recloser Refurbishment - Planned | 66 | REPEX | AMP.3.1.13 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 751.65 | 755.3 | 755.3 | 755.3 | 755.3 | 755.3 | [6 empty] | 100%
|  | Recloser Replacement - Planned | 67 | REPEX | AMP.3.1.13 | 2075.326 | 2993.703 | 3288.0385 | 3229.501 | 3759.4865 | 3640.045 | 2490 | 2140 | 2150.5 | 2151.5 | 2152.5 | 2153.5 | 2154 | [6 empty] | 100%
|  | Services Replacement - Planned | 68 | REPEX | AMP.3.1.08 | 757.9035 | 1417.1255 | 2026.93 | 2356.4315 | 4303.0388 | 4457.4483 | 3029.7243 | 3389.1728 | 3568.897 | 3568.897 | 3568.897 | 3568.897 | 3568.897 | [5 empty] | 15% | 85%
|  | Strategic Line Maintenance Spares | 69 | REPEX | Historical | 47.6865 | 0.1455 | 0.522 | 0.522 | 37.026 | 60.776 | 23.75 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Switchgear - Ground Level - Planned | 70 | REPEX | AMP.3.1.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Switchgear - Overhead - Planned | 71 | REPEX | AMP.3.1.07 | 1546.022 | 2407.6815 | 2397.178 | 2706.3905 | 3567.5129 | 3289.6369 | 2887.5 | 2962.5 | 3000 | 3000 | 3000 | 3000 | 3000 | [6 empty] | 100%
|  | Transformers - Planned | 72 | REPEX | AMP.3.1.01 | 1639.611 | 1624.1025 | 1638.8155 | 3202.7155 | 4224.2879 | 2633.0819 | 2224.6042 | 2873.8125 | 3198.4167 | 3198.4167 | 3198.4167 | 3198.4167 | 3198.4167 |  |  |  |  | 25% |  | 75%
|  | Poles - Planned plating | 73 | REPEX | AMP.3.1.05 | 2981.338 | 3248.46 | 3098.2525 | 5559.488 | 6705.7741 | 5647.7606 | 6142.6869 | 7028.0607 | 7470.7476 | 7470.7476 | 7470.7476 | 7470.7476 | 7470.7476 | [6 empty] | 100%
|  | Recloser Maintenance - Planned | 74 | REPEX | AMP.3.1.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Pole Replacement Projects | 75 |  |  | 35.693 | 52.8025 | 29.503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | CBD ducts & manholes | 76 |  |  | 0 | 0 | 0 | 839.4105 | 1112.447 | 1223.0365 | 2170 | 2710 | 2980 | 2980 | 2980 | 2980 | 2980 | [6 empty] | 100%
|  | Cables - CBD 11kV PILC cable replacements | 77 |  |  | 0 | 0 | 0 | 0 | 0 | 799.3202 | 1598.6404 | 2397.9606 | 3197.2807 | 3197.2807 | 3197.2807 | 3197.2807 | 3197.2807 | [6 empty] | 100%
|  | Services - Aluminium neutral screen service line replacements | 78 |  |  | 0 | 0 | 0 | 0 | 0 | 210.3848 | 420.7695 | 631.1543 | 841.5391 | 841.5391 | 841.5391 | 841.5391 | 841.5391 | [6 empty] | 100%
100%
|  | Unplanned | [22 empty] | 100%
|  | Cable Replacement - Unplanned | 91 | REPEX | AMP.3.1.09 | 3526.3255 | 3250.205 | 3213.2165 | 4061.058 | 4043.4645 | 3613.8995 | 2109.4 | 624.4 | 640 | 640 | 640 | 640 | 640 |  |  |  | 15% |  | 10% | 75%
|  | Line Ancillary Equipment - Unplanned (incl LFIs, fences, gates, signs etc) | 92 | REPEX | AMP.3.1.20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Line Regulation - Unplanned (incl regulators, capacitors) | 93 | REPEX | AMP.3.1.19 | -7.404 | 1.0375 | 5.0355 | 1.73 | 10.5231 | 34.2731 | 91.25 | 135 | 135 | 157.5 | 180 | 180 | 180 | [6 empty] | 100%
|  | Overhead Line Components - Unplanned (incl insulators, Xarms, pole earths) | 94 | REPEX | AMP.3.1.06 | 9135.7165 | 9470.686 | 6548.445 | 6455.7565 | 5700.8842 | 5799.5337 | 5918.8157 | 6356.447 | 6575.2627 | 6575.2627 | 6575.2627 | 6575.2627 | 6575.2627 | [6 empty] | 100%
|  | Poles - Unplanned | 95 | REPEX | AMP.3.1.05 | 2092.3285 | 1777.652 | 2524.3715 | 2987.4065 | 2456.5042 | 2390.3377 | 2477.5 | 2492.5 | 2500 | 2500 | 2500 | 2500 | 2500 | [6 empty] | 100%
|  | Recloser Replacement - Unplanned | 96 | REPEX | AMP.3.1.13 | 1666.392 | 1325.8755 | 1111.365 | 1258.024 | 1583.8279 | 1619.1289 | 1384.375 | 1208.125 | 1120 | 1120 | 1120 | 1120 | 1120 | [6 empty] | 100%
|  | Services Replacement - Unplanned | 97 | REPEX | AMP.3.1.08 | 3128.9665 | 3428.094 | 3858.6875 | 3938.8635 | 3670.9551 | 3478.9591 | 3552.5 | 4197.5 | 4520 | 4520 | 4520 | 4520 | 4520 | [5 empty] | 15% | 85%
|  | Switchgear - Ground Level - Unplanned | 98 | REPEX | AMP.3.1.03 | 561.7055 | 441.775 | 569.847 | 614.015 | 661.4604 | 665.9789 | 499 | 433 | 400 | 400 | 400 | 400 | 400 | [6 empty] | 100%
|  | Switchgear - Overhead - Unplanned | 99 | REPEX | AMP.3.1.07 | 2746.3511 | 2597.204 | 1892.079 | 1930.076 | 2061.2406 | 1934.1006 | 2300 | 3100 | 3500 | 3500 | 3500 | 3500 | 3500 | [6 empty] | 100%
|  | Transformers - Unplanned | 100 | REPEX | AMP.3.1.01 | 4484.3205 | 4657.315 | 4920.111 | 5210.749 | 5195.3716 | 5137.1421 | 5243.75 | 5281.25 | 5300 | 5300 | 5300 | 5300 | 5300 |  |  |  |  | 25% |  | 75%
|  | Other | 101 |  |  | 184.1795 | 100.794 | 13.583 | 221.2195 | 286.96 | 80.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
Substations
|  | Auxillary DC Supplies excl AC - Battery Banks & Chargers | 106 | REPEX | AMP.3.2.08 | 228.1555 | 223.296 | 221.8825 | 314.6555 | 437.8437 | 555.3857 | 636.55 | 646.1 | 646.1 | 646.1 | 646.1 | 364.05 | 93.85 | [6 empty] | 100%
|  | Capacitor Banks - CAPACITY UPGRADE? | 107 | REPEX | AMP.3.2.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Circuit Breakers Planned Replacement | 108 | REPEX | AMP.3.2.05 | 6266.1555 | 4494.1915 | 4213.164 | 10752.015 | 19781.96 | 17948.654 | 11875.5083 | 10935.4828 | 10740.9491 | 11615.7491 | 11462.7491 | 10515.9491 | 10457.9452 |  |  | 10% |  |  |  | 90%
|  | Circuit Breakers Planned Refurb | 109 | REPEX | AMP.3.2.02 | 0 | 0 | 0 | 0 | 0 | 0 | 622.8343 | 1215.0536 | 1193.4388 | 1290.6388 | 1273.6388 | 1168.4388 | 1161.9939 |  |  | 25% |  |  |  | 75%
|  | Mobile Substations | 110 | REPEX | AMP.3.2.13 | 135.2245 | 0 | 0 | 0 | 0 | 0 | 150 | 300 | 300 | 300 | 300 | 300 | 300 |  |  | 25% |  |  |  | 75%
|  | Protection Relays (Replace 33kV/66kV Fuses, incl Fault Thrower) | 111 | REPEX | AMP.3.2.14 | 0 | 0 | 0 | 0 | 1282.3555 | 1282.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Substation Insurance Spares & Asset Mgt | 112 | REPEX | Historical | 1259.7205 | 1431.882 | 1234.866 | 1157.965 | 1490.9065 | 1620.579 | 1560 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | [6 empty] | 100%
|  | Substation Infrastructure - Civil (incl buildings, structures) | 113 | REPEX | AMP3.2.16 | 314.7875 | 672.1055 | 889.9465 | 1713.522 | 1707.7585 | 1113.5325 | 1462.5 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | [6 empty] | 100%
|  | Substation Transformer Repl. | 114 | REPEX | AMP.3.2.01 | 3553.5125 | 2015.8955 | 2112.932 | 2358.7535 | 3041.5305 | 4209.0295 | 5113.8158 | 4677.6316 | 4610.1316 | 5370.1316 | 4407.6316 | 3512.6316 | 3512.6316 |  |  | 25% |  |  |  | 75%
|  | TF Refurb (18665 & 18977) | 115 |  |  | 674 | 419.5 | 53 | 53 | 0 | 0 | 800 | 1575 | 1250 | 950 | 950 | 950 | 950 | [6 empty] | 100%
|  | Planned Transformer Refurbishment - also done under 18665 | 116 |  |  | 323.409 | 458.8175 | 387.4065 | 0.0555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Surge Arrester | 117 | REPEX | AMP.3.2.03 | 149.0255 | 211.7105 | 250.3485 | 261.9395 | 194.716 | 247.6495 | 327.407 | 312.8139 | 343.3324 | 343.3324 | 335.7027 | 213.629 | 53.4073 | [6 empty] | 100%
|  |  | 118 | REPEX | AMP.3.2.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Carryover (subs) | 119 | REPEX | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | AC Panels + auxilary supply | 120 | REPEX | AMP 3.2.22 | 27.0345 | 63.1005 | 147.1525 | 134.66 | 291.362 | 469.6635 | 561.875 | 720 | 720 | 720 | 720 | 597.5 | 500 | [6 empty] | 100%
|  | Protection Asset Replacement | 121 | REPEX | AMP.3.2.14 | 2167.657 | 3022.672 | 2700.552 | 2294.019 | 1890.5011 | 1532.2881 | 2445 | 2800 | 2850 | 2650 | 2450 | 2500 | 2500 | [6 empty] | 100%
|  | Unplanned CB Replacement | 122 | REPEX |  | 1252.761 | 862.0935 | 1327.4475 | 1153.4205 | 541.907 | 559.981 | 594.5 | 467 | 467 | 467 | 467 | 467 | 467 |  |  | 25% |  |  |  | 75%
|  | Standby Power Station | 123 | REPEX |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Unplanned Substation Asset Repl - PROTECTION | 124 |  |  | 58.958 | 248.5845 | 626.87 | 1292.632 | 1499.1725 | 615.1785 | 400 | 800 | 800 | 800 | 800 | 800 | 800 | [6 empty] | 100%
|  | Other (sub cables) | 125 |  |  | 546.693 | 496.434 | 770.149 | 1659.054 | 1763.392 | 686.848 | 587.4383 | 714.3766 | 253.8766 | 264.3766 | 264.3766 | 222.3766 | 117.3766 | [6 empty] | 100%
|  | Northfield 66kV GIS Switchboard replacement (1/3rd) | 126 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1250 | 4200 | 5000 | 2000 | 0 | 0 |  |  | 25% |  |  |  | 75%
|  | MOD3C Substation Upgrades (trf to 18665) | 127 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Substation Standards Templates and CU Developments | 128 |  |  | 0 | 0 | 0 | 0 | 80.5946 | 80.5946 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Relay Replace on Failure | 129 |  |  | 0 | 0 | 0 | 0 | 117.0781 | 497.0781 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Cable replacement & Cable Termination Support upgrade (tfr to other) | 130 |  |  | 0 | 0 | 0 | 0 | 126.844 | 483.094 | 356.25 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | GIS Assessment and Refurbishment | 131 |  |  | 0 | 0 | 0 | 0 | 0 | 118.75 | 118.75 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Transformer planned replacement due to condition | 132 |  |  | 0 | 0 | 0 | 0 | 0 | 2232.5 | 2232.5 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 100%
|  | Replace/Refurbish (total) |  |  | total | 83021.2526 | 84095.5525 | 83034.978 | 102202.114 | 127064.791 | 128705.4119 | 117639.7928 | 117049.3865 | 124001.3657 | 126067.3657 | 121760.7361 | 117306.1124 | 116609.2418
|  | Sub-Trans |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Zone S/Stn |  |  |  | 1861.99 | 1168.9164 | 1281.4113 | 1953.245 | 2874.0554 | 2987.118 | 2820.3383 | 3070.9696 | 3766.7375 | 4268.5175 | 3258.3425 | 2413.6125 | 2406.2009
|  | HV Feeder |  |  |  | 1104.593 | 1007.1762 | 897.2696 | 1436.3335 | 2339.3433 | 3171.8881 | 2214.1698 | 783.4793 | 729.619 | 729.619 | 729.619 | 729.619 | 729.619
|  | Dist T/F |  |  |  | 1530.9829 | 1570.3544 | 1639.7316 | 2103.3661 | 2354.9149 | 1942.556 | 1867.0885 | 2038.7656 | 2124.6042 | 2124.6042 | 2124.6042 | 2124.6042 | 2124.6042
|  | LV Feeder |  |  |  | 1319.4258 | 1398.2337 | 1481.0224 | 1901.8499 | 2755.6613 | 3305.0532 | 2463.4468 | 1660.3204 | 1699.7472 | 1699.7472 | 1699.7472 | 1699.7472 | 1699.7472
[6 empty] | 5816.9917 | 5144.6807 | 5299.4349 | 7394.7945 | 10323.9748 | 11406.6153 | 9365.0434 | 7553.5349 | 8320.7079 | 8822.4879 | 7812.3129 | 6967.5829 | 6960.1713
|  | not augmentation $000 nominal |  |  |  | 77204.2609 | 78950.8718 | 77735.5431 | 94807.3195 | 116740.8161 | 117298.7967 | 108274.7494 | 109495.8516 | 115680.6578 | 117244.8778 | 113948.4232 | 110338.5294 | 109649.0705
|  | CPI $ 2020 | [5 empty] | 106.6 | 108.4 | 110 | 112.1 | 114.342 | 117.1662 | 120.0603 | 123.0257 | 126.0645 | 129.1783 | 132.369
|  | CPI Adj $ 2020 | [5 empty] | 1.0726 | 1.0548 | 1.0395 | 1.02 | 1 | 0.9759 | 0.95237 | 0.92942 | 0.90701 | 0.88515 | 0.86381
|  | Sub-Trans | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Zone S/Stn | [5 empty] | 1374.4759 | 2060.3131 | 2987.5022 | 3046.8604 | 2820.3383 | 2996.945 | 3587.3346 | 3967.2252 | 2955.3559 | 2136.4064 | 2078.5069
|  | HV Feeder | [5 empty] | 962.4353 | 1515.0668 | 2431.6836 | 3235.3258 | 2214.1698 | 764.5938 | 694.8686 | 678.119 | 661.7732 | 645.8214 | 630.2542
|  | Dist T/F | [5 empty] | 1758.8198 | 2218.6632 | 2447.8698 | 1981.4071 | 1867.0885 | 1989.622 | 2023.4131 | 1974.6395 | 1927.0416 | 1880.591 | 1835.2601
|  | LV Feeder | [5 empty] | 1588.5841 | 2006.1007 | 2864.4347 | 3371.1542 | 2463.4468 | 1620.299 | 1618.7913 | 1579.771 | 1541.6912 | 1504.5293 | 1468.2632
|  | Repl Augmentation Capex Real $ 2020 000's | [5 empty] | 5684.3151 | 7800.1438 | 10731.4903 | 11634.7476 | 9365.0434 | 7371.4598 | 7924.4076 | 8199.7548 | 7085.8619 | 6167.3481 | 6012.2843
|  | Replacement Augmentation | [5 empty] | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
|  | Sub-Trans | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Zone S/Stn | [5 empty] | 1374475.8725 | 2060313.0972 | 2987502.1757 | 3046860.3827 | 2820338.3357 | 2996945.0417 | 3587334.5722 | 3967225.2311 | 2955355.8963 | 2136406.3729 | 2078506.8746 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981 | 2953628.9981
|  | HV Feeder | [5 empty] | 962435.3045 | 1515066.8099 | 2431683.5543 | 3235325.8309 | 2214169.7526 | 764593.7911 | 694868.5706 | 678119.0305 | 661773.2317 | 645821.4421 | 630254.1642 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717 | 679238.3717
|  | Dist T/F | [5 empty] | 1758819.8261 | 2218663.1869 | 2447869.8052 | 1981407.1373 | 1867088.5438 | 1989621.9687 | 2023413.1037 | 1974639.5079 | 1927041.5808 | 1880590.9835 | 1835260.0601 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675 | 1938427.8675
|  | LV Feeder | [5 empty] | 1588584.0563 | 2006100.7497 | 2864434.7429 | 3371154.2149 | 2463446.8077 | 1620299.0369 | 1618791.3307 | 1579770.9873 | 1541691.2143 | 1504529.3396 | 1468263.2376 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244 | 1555557.5244
|  | Repl Augmentation Capex Real $ 2020 | [5 empty] | 5684315.0594 | 7800143.8437 | 10731490.2781 | 11634747.5658 | 9365043.4398 | 7371459.8384 | 7924407.5772 | 8199754.7568 | 7085861.9232 | 6167348.1382 | 6012284.3365 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617 | 7126852.7617
|  | Notes | [5 empty] | 5684.3151 2016: 2026/27 to 2039/40 based on the average spend over the 6 year period 2020/21 to 2025/26
LRMC sample shaded

## Opex
Incremental opex is calculated as a proportion of the incremental capex cost.
| Opex proportions by voltage |  |  | Opex profile for new assets
| Voltage | Prop'n |  | Year | 0 | 1 | 2 | 3 | 4
| ST | 1.5% |  | Prop'n | 0% | 40% | 40% | 40% | 100%
| HV bus | 1.5% |  | Lag | -4 | -3 | -2 | -1 | 0
| HV net | 2% |  | Annual prop'n | 60% | 0% | 0% | 40% | 0%
| LV bus | 2%
| LV net | 2%
|  |  | Total | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
|  |  | 2015/16-2019/20 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40
Total growth related capex $M 2020 real
| ST |  | 45.3148 | 7.6793 | 8.5207 | 11.4171 | 9.6409 | 8.0567 | 10.4272 | 7.8892 | 2.0779 | 1.1573 | 3.9442 | 6.2816 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963
| HV bus |  | 96.0273 | 27.2047 | 23.8441 | 19.6964 | 13.9539 | 11.3283 | 8.4864 | 7.8635 | 8.9582 | 8.402 | 6.0311 | 4.3676 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514
| HV net |  | 23.9075 | 2.316 | 4.1217 | 6.2079 | 5.2229 | 6.0389 | 5.7307 | 3.2365 | 2.9308 | 3.5325 | 3.6952 | 3.4549 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634
| LV bus |  | 36.0888 | 6.9592 | 7.5161 | 7.4512 | 6.5383 | 7.6241 | 8.8392 | 8.9364 | 8.9441 | 9.1287 | 9.1211 | 9.0049 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957
| LV net |  | 21.628 | 3.3721 | 3.973 | 4.7415 | 4.9428 | 4.5987 | 4.2211 | 4.214 | 4.1682 | 4.1221 | 4.0759 | 4.0036 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341
| Total |  | 222.9664 | 47.5313 | 47.9756 | 49.5141 | 40.2987 | 37.6467 | 37.7045 | 32.1397 | 27.0792 | 26.3426 | 26.8674 | 27.1126 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541
Total incremental annual opex $M 2020 real
| ST |  | 0.29266 | 0 | 0.046076 | 0.051124 | 0.068503 | 0.12696 | 0.12503 | 0.16532 | 0.1341 | 0.084978 | 0.10079 | 0.094668 | 0.056391 | 0.042194 | 0.067276 | 0.088312 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444
| HV bus |  | 0.75304 | 0 | 0.16323 | 0.14306 | 0.11818 | 0.32857 | 0.28257 | 0.22819 | 0.17277 | 0.1557 | 0.12679 | 0.10696 | 0.10683 | 0.11973 | 0.098388 | 0.083417 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027
| HV net |  | 0.17074 | 0 | 0.018528 | 0.032974 | 0.049663 | 0.069576 | 0.097772 | 0.12034 | 0.088567 | 0.095913 | 0.097028 | 0.068399 | 0.062809 | 0.072497 | 0.074449 | 0.071566 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268
| LV bus |  | 0.31123 | 0 | 0.055673 | 0.060128 | 0.059609 | 0.13582 | 0.15119 | 0.16013 | 0.14995 | 0.16304 | 0.1791 | 0.18021 | 0.17937 | 0.18151 | 0.18142 | 0.18002 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991
| LV net |  | 0.1767 | 0 | 0.026976 | 0.031784 | 0.037932 | 0.080007 | 0.084465 | 0.090667 | 0.093025 | 0.08853 | 0.08363 | 0.083175 | 0.082047 | 0.082539 | 0.081984 | 0.081116 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683
| Total |  | 1.7044 | 0 | 0.31048 | 0.31908 | 0.33389 | 0.74092 | 0.74102 | 0.76464 | 0.63841 | 0.58817 | 0.58734 | 0.53341 | 0.48744 | 0.49847 | 0.50352 | 0.50444 | 0.52758 | 0.52758 | 0.52758 | 0.52758 | 0.52758 | 0.52758 | 0.52758 | 0.52758 | 0.52758 | 0.52758
| Augmentation Related Incremental Opex $ 2020 |  |  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
| ST |  |  | 0 | 46075.9849 | 51124.3118 | 68502.7683 | 126959.1076 | 125026.9677 | 165317.3416 | 134102.9549 | 84978.3908 | 100788.8681 | 94668.2293 | 56391.3367 | 42193.6912 | 67275.5752 | 88312.3782 | 79443.9122 | 79443.9122 | 79443.9122 | 79443.9122 | 79443.9122 | 79443.9122 | 79443.9122 | 79443.9122 | 79443.9122 | 79443.9122
| HV bus |  |  | 0 | 163228.1838 | 143064.4804 | 118178.4523 | 328565.6072 | 282566.3007 | 228185.818 | 172765.901 | 155703.4806 | 126788.9886 | 106957.724 | 106829.3289 | 119726.3299 | 98388.2134 | 83417.1554 | 110271.6519 | 110271.6519 | 110271.6519 | 110271.6519 | 110271.6519 | 110271.6519 | 110271.6519 | 110271.6519 | 110271.6519 | 110271.6519
| HV net |  |  | 0 | 18528.1392 | 32973.9877 | 49663.0503 | 69575.5301 | 97772.3396 | 120340.0269 | 88567.0685 | 95913.3509 | 97027.908 | 68399.4041 | 62808.8442 | 72496.968 | 74449.2833 | 71566.4319 | 75268.4293 | 75268.4293 | 75268.4293 | 75268.4293 | 75268.4293 | 75268.4293 | 75268.4293 | 75268.4293 | 75268.4293 | 75268.4293
| LV bus |  |  | 0 | 55673.3324 | 60128.4908 | 59609.3325 | 135816.2704 | 151185.4446 | 160127.5004 | 149950.9429 | 163041.7991 | 179099.9902 | 180206.1728 | 179368.3483 | 181510.5442 | 181419.2423 | 180024.8027 | 179914.8436 | 179914.8436 | 179914.8436 | 179914.8436 | 179914.8436 | 179914.8436 | 179914.8436 | 179914.8436 | 179914.8436 | 179914.8436
| LV net |  |  | 0 | 26976.4532 | 31783.7365 | 37932.312 | 80006.7675 | 84465.1791 | 90666.9499 | 93025.1675 | 88529.9012 | 83629.8467 | 83175.1483 | 82046.7373 | 82538.8031 | 81983.7589 | 81115.7593 | 82682.7932 | 82682.7932 | 82682.7932 | 82682.7932 | 82682.7932 | 82682.7932 | 82682.7932 | 82682.7932 | 82682.7932 | 82682.7932
| Incremental Opex $ 2020 |  |  | 0 | 310482.0934 | 319075.0073 | 333885.9155 | 740923.2828 | 741016.2318 | 764637.6368 | 638412.0348 | 588166.9225 | 587335.6016 | 533406.6785 | 487444.5954 | 498466.3365 | 503516.073 | 504436.5275 | 527581.6303 | 527581.6303 | 527581.6303 | 527581.6303 | 527581.6303 | 527581.6303 | 527581.6303 | 527581.6303 | 527581.6303 | 527581.6303
| Notes |  |  | 2016: LRMC sample shaded

## Demand
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
|  | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40
Split of Demand across Tariff Classes - Maximum Demand at Transmission Exit (from Pricing Model using 2018/18 data) |  | 3 2017/18: MW at Exit
ST | Major Business sub-transmission | 3 2017/18: 73; 4 2018/19: 2.205%
HV Bus | Major Business zone s/stn | 3 2017/18: 71; 4 2018/19: 2.144%
HV line | HV business | 3 2017/18: 176; 4 2018/19: 5.316%
LV Bus | large LV business | 3 2017/18: 809; 4 2018/19: 24.43%
LV line | combines small business and residential | 3 2017/18: 2182; 4 2018/19: 65.9%
[5 empty] | 3311 | 100%
Table 3.4.3.2 Annual system maximum demand characteristics at the transmission connection point – MW measure
DOPSD0111 | Coincident Weather Adjusted System Annual Maximum Demand 10% POE | 0 2014/15: 2813.4199; 1 2015/16: 2826.3744; 2 2016/17: 2840.7647; 3 2017/18: 2827.4007; 4 2018/19: 2885.5996; 5 2019/20: 2898.6093; 6 2020/21: 2912.5873; 7 2021/22: 2920.6757; 8 2022/23: 2928.6951; 9 2023/24: 2936.7613; 10 2024/25: 2944.9206
System maximum demand |  | 2813.4199 | 2826.3744 | 2840.7647 | 2827.4007 | 2885.5996 | 2898.6093 | 2912.5873 | 2920.6757 | 2928.6951 | 2936.7613 | 2944.9206 | 2971.0579 | 2985.3886 | 2999.7193 | 3014.05 | 3028.3808 | 3042.7115 | 3057.0422 | 3071.373 | 3085.7037 | 3100.0344 | 3114.3651 | 3128.6959 | 3143.0266 | 3157.3573 | 3171.688
|  |  | 0.4605% | 0.5091% | -0.4704% | 2.058% | 0.4508% | 0.4822% | 0.2777% | 0.2746% | 0.2754% | 0.2778% | 0.8875% | 0.4823% | 0.48% | 0.4777% | 0.4755% | 0.4732% | 0.471% | 0.4688% | 0.4666% | 0.4644% | 0.4623% | 0.4601% | 0.458% | 0.456% | 0.4539%
Maximum Demand MW split by voltage level contribution
ST |  | 62.0295 | 62.3151 | 62.6324 | 62.3377 | 63.6209 | 63.9077 | 64.2159 | 64.3942 | 64.571 | 64.7489 | 64.9288 | 65.5051 | 65.821 | 66.137 | 66.4529 | 66.7689 | 67.0849 | 67.4008 | 67.7168 | 68.0327 | 68.3487 | 68.6646 | 68.9806 | 69.2966 | 69.6125 | 69.9285
HV Bus |  | 60.3301 | 60.6078 | 60.9164 | 60.6299 | 61.8779 | 62.1568 | 62.4566 | 62.63 | 62.802 | 62.9749 | 63.1499 | 63.7104 | 64.0177 | 64.325 | 64.6323 | 64.9396 | 65.2469 | 65.5542 | 65.8615 | 66.1688 | 66.4761 | 66.7834 | 67.0907 | 67.398 | 67.7053 | 68.0126
HV line |  | 149.5506 | 150.2392 | 151.0041 | 150.2937 | 153.3874 | 154.0789 | 154.8219 | 155.2519 | 155.6781 | 156.1069 | 156.5406 | 157.93 | 158.6918 | 159.4535 | 160.2153 | 160.9771 | 161.7388 | 162.5006 | 163.2623 | 164.0241 | 164.7859 | 165.5476 | 166.3094 | 167.0712 | 167.8329 | 168.5947
LV Bus |  | 687.4227 | 690.588 | 694.1041 | 690.8388 | 705.0589 | 708.2377 | 711.653 | 713.6293 | 715.5887 | 717.5596 | 719.5532 | 725.9395 | 729.4411 | 732.9426 | 736.4441 | 739.9456 | 743.4472 | 746.9487 | 750.4502 | 753.9518 | 757.4533 | 760.9548 | 764.4563 | 767.9579 | 771.4594 | 774.9609
LV line |  | 1854.087 | 1862.6243 | 1872.1077 | 1863.3006 | 1901.6546 | 1910.2281 | 1919.4399 | 1924.7703 | 1930.0552 | 1935.3709 | 1940.7481 | 1957.9729 | 1967.4171 | 1976.8612 | 1986.3054 | 1995.7496 | 2005.1937 | 2014.6379 | 2024.0821 | 2033.5263 | 2042.9704 | 2052.4146 | 2061.8588 | 2071.3029 | 2080.7471 | 2090.1913
|  | 2813.4199 | 2826.3744 | 2840.7647 | 2827.4007 | 2885.5996 | 2898.6093 | 2912.5873 | 2920.6757 | 2928.6951 | 2936.7613 | 2944.9206 | 2971.0579 | 2985.3886 | 2999.7193 | 3014.05 | 3028.3808 | 3042.7115 | 3057.0422 | 3071.373 | 3085.7037 | 3100.0344 | 3114.3651 | 3128.6959 | 3143.0266 | 3157.3573 | 3171.688
Annual demand increment MW by voltage level |  |  | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40
ST |  |  | 0.28562 | 0.31727 | -0.29465 | 1.2832 | 0.28683 | 0.30818 | 0.17833 | 0.17681 | 0.17784 | 0.1799 | 0.57627 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596
HV Bus |  |  | 0.27779 | 0.30858 | -0.28657 | 1.248 | 0.27897 | 0.29974 | 0.17344 | 0.17197 | 0.17297 | 0.17497 | 0.56048 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073
HV line |  |  | 0.68861 | 0.76493 | -0.71038 | 3.0936 | 0.69154 | 0.74302 | 0.42995 | 0.42628 | 0.42877 | 0.43372 | 1.3894 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177
LV Bus |  |  | 3.1653 | 3.5161 | -3.2653 | 14.2201 | 3.1787 | 3.4154 | 1.9763 | 1.9594 | 1.9709 | 1.9936 | 6.3863 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015
LV line |  |  | 8.5372 | 9.4834 | -8.8071 | 38.3539 | 8.5736 | 9.2117 | 5.3304 | 5.2849 | 5.3157 | 5.3771 | 17.2248 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442
|  |  | 12.9545 | 14.3903 | -13.364 | 58.1989 | 13.0097 | 13.978 | 8.0884 | 8.0194 | 8.0662 | 8.1594 | 26.1372 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307
Note on M5: James Bennett: not co-incident, but maximum for ecash tariff class exiting at that voltage level
Note on J15: James Bennett: was 2862, extrapolate
Note on N15: James Bennett: from 2020-25 Reset RIN
Note on U18: James Bennett: forecast based on growth last 10 years

## LRMC - AIC
Filename: LRMC 2019 v1F.xlsx
|  | WACC | Life |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Real framework |  | 2.887% | 50 |  | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40
NPV20
Incremental MW for LRMC calculation |  |  |  | MW
| ST |  | 5.3916 |  | 0 | 0.28562 | 0.31727 | -0.29465 | 1.2832 | 0.28683 | 0.30818 | 0.17833 | 0.17681 | 0.17784 | 0.1799 | 0.57627 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596 | 0.31596
| HV bus |  | 5.2439 |  | 0 | 0.27779 | 0.30858 | -0.28657 | 1.248 | 0.27897 | 0.29974 | 0.17344 | 0.17197 | 0.17297 | 0.17497 | 0.56048 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073 | 0.3073
| HV net |  | 12.9989 |  | 0 | 0.68861 | 0.76493 | -0.71038 | 3.0936 | 0.69154 | 0.74302 | 0.42995 | 0.42628 | 0.42877 | 0.43372 | 1.3894 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177 | 0.76177
| LV bus |  | 59.7504 |  | 0 | 3.1653 | 3.5161 | -3.2653 | 14.2201 | 3.1787 | 3.4154 | 1.9763 | 1.9594 | 1.9709 | 1.9936 | 6.3863 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015 | 3.5015
| LV net |  | 161.1562 |  | 0 | 8.5372 | 9.4834 | -8.8071 | 38.3539 | 8.5736 | 9.2117 | 5.3304 | 5.2849 | 5.3157 | 5.3771 | 17.2248 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442 | 9.4442
| Total |  | 244.5409 |  | 0 | 12.9545 | 14.3903 | -13.364 | 58.1989 | 13.0097 | 13.978 | 8.0884 | 8.0194 | 8.0662 | 8.1594 | 26.1372 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307 | 14.3307
Total growth related capex real |  |  |  | $M
| ST |  |  |  |  | 7.6793 | 8.5207 | 11.4171 | 9.6409 | 8.0567 | 10.4272 | 7.8892 | 2.0779 | 1.1573 | 3.9442 | 6.2816 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963 | 5.2963
| HV bus |  |  |  |  | 27.2047 | 23.8441 | 19.6964 | 13.9539 | 11.3283 | 8.4864 | 7.8635 | 8.9582 | 8.402 | 6.0311 | 4.3676 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514 | 7.3514
| HV net |  |  |  |  | 2.316 | 4.1217 | 6.2079 | 5.2229 | 6.0389 | 5.7307 | 3.2365 | 2.9308 | 3.5325 | 3.6952 | 3.4549 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634 | 3.7634
| LV bus |  |  |  |  | 6.9592 | 7.5161 | 7.4512 | 6.5383 | 7.6241 | 8.8392 | 8.9364 | 8.9441 | 9.1287 | 9.1211 | 9.0049 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957 | 8.9957
| LV net |  |  |  |  | 3.3721 | 3.973 | 4.7415 | 4.9428 | 4.5987 | 4.2211 | 4.214 | 4.1682 | 4.1221 | 4.0759 | 4.0036 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341 | 4.1341
| Total |  |  |  |  | 47.5313 | 47.9756 | 49.5141 | 40.2987 | 37.6467 | 37.7045 | 32.1397 | 27.0792 | 26.3426 | 26.8674 | 27.1126 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541 | 29.541
Incremental annual capex |  |  |  | $M
| ST |  |  |  |  | 0.29207 | 0.32407 | 0.43423 | 0.36668 | 0.30643 | 0.39658 | 0.30005 | 0.079031 | 0.044018 | 0.15001 | 0.23891 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144 | 0.20144
| HV bus |  |  |  |  | 1.0347 | 0.90687 | 0.74912 | 0.53072 | 0.43085 | 0.32277 | 0.29908 | 0.34071 | 0.31956 | 0.22938 | 0.16612 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796 | 0.2796
| HV net |  |  |  |  | 0.088086 | 0.15676 | 0.23611 | 0.19865 | 0.22968 | 0.21796 | 0.1231 | 0.11147 | 0.13435 | 0.14054 | 0.1314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314 | 0.14314
| LV bus |  |  |  |  | 0.26468 | 0.28586 | 0.28339 | 0.24867 | 0.28997 | 0.33619 | 0.33988 | 0.34018 | 0.3472 | 0.34691 | 0.34249 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214 | 0.34214
| LV net |  |  |  |  | 0.12825 | 0.15111 | 0.18034 | 0.18799 | 0.1749 | 0.16054 | 0.16027 | 0.15853 | 0.15678 | 0.15502 | 0.15227 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724 | 0.15724
| Total |  |  |  |  | 1.8078 | 1.8247 | 1.8832 | 1.5327 | 1.4318 | 1.434 | 1.2224 | 1.0299 | 1.0019 | 1.0219 | 1.0312 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235 | 1.1235
Incremental opex p.a. |  |  |  | $M p.a.
| ST |  |  |  |  | 0 | 0.046076 | 0.051124 | 0.068503 | 0.12696 | 0.12503 | 0.16532 | 0.1341 | 0.084978 | 0.10079 | 0.094668 | 0.056391 | 0.042194 | 0.067276 | 0.088312 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444 | 0.079444
| HV bus |  |  |  |  | 0 | 0.16323 | 0.14306 | 0.11818 | 0.32857 | 0.28257 | 0.22819 | 0.17277 | 0.1557 | 0.12679 | 0.10696 | 0.10683 | 0.11973 | 0.098388 | 0.083417 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027 | 0.11027
| HV net |  |  |  |  | 0 | 0.018528 | 0.032974 | 0.049663 | 0.069576 | 0.097772 | 0.12034 | 0.088567 | 0.095913 | 0.097028 | 0.068399 | 0.062809 | 0.072497 | 0.074449 | 0.071566 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268 | 0.075268
| LV bus |  |  |  |  | 0 | 0.055673 | 0.060128 | 0.059609 | 0.13582 | 0.15119 | 0.16013 | 0.14995 | 0.16304 | 0.1791 | 0.18021 | 0.17937 | 0.18151 | 0.18142 | 0.18002 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991 | 0.17991
| LV net |  |  |  |  | 0 | 0.026976 | 0.031784 | 0.037932 | 0.080007 | 0.084465 | 0.090667 | 0.093025 | 0.08853 | 0.08363 | 0.083175 | 0.082047 | 0.082539 | 0.081984 | 0.081116 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683 | 0.082683
| Total |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total incremental costs |  |  |  | $M p.a.
| ST |  | 4.6847 |  |  | 0.29207 | 0.37015 | 0.48536 | 0.43518 | 0.43339 | 0.52161 | 0.46537 | 0.21313 | 0.129 | 0.2508 | 0.33358 | 0.25783 | 0.24363 | 0.26871 | 0.28975 | 0.28088 | 0.28088 | 0.28088 | 0.28088 | 0.28088 | 0.28088 | 0.28088 | 0.28088 | 0.28088 | 0.28088
| HV bus |  | 6.8181 |  |  | 1.0347 | 1.0701 | 0.89219 | 0.64889 | 0.75942 | 0.60533 | 0.52726 | 0.51348 | 0.47526 | 0.35617 | 0.27307 | 0.38643 | 0.39933 | 0.37799 | 0.36302 | 0.38987 | 0.38987 | 0.38987 | 0.38987 | 0.38987 | 0.38987 | 0.38987 | 0.38987 | 0.38987 | 0.38987
| HV net |  | 3.4807 |  |  | 0.088086 | 0.17529 | 0.26908 | 0.24831 | 0.29926 | 0.31573 | 0.24344 | 0.20004 | 0.23027 | 0.23757 | 0.1998 | 0.20594 | 0.21563 | 0.21759 | 0.2147 | 0.2184 | 0.2184 | 0.2184 | 0.2184 | 0.2184 | 0.2184 | 0.2184 | 0.2184 | 0.2184 | 0.2184
| LV bus |  | 7.4667 |  |  | 0.26468 | 0.34154 | 0.34352 | 0.30828 | 0.42579 | 0.48737 | 0.50001 | 0.49013 | 0.51024 | 0.52601 | 0.52269 | 0.52151 | 0.52365 | 0.52356 | 0.52216 | 0.52205 | 0.52205 | 0.52205 | 0.52205 | 0.52205 | 0.52205 | 0.52205 | 0.52205 | 0.52205 | 0.52205
| LV net |  | 3.6299 |  |  | 0.12825 | 0.17808 | 0.21212 | 0.22592 | 0.25491 | 0.24501 | 0.25094 | 0.25156 | 0.24531 | 0.23865 | 0.23544 | 0.23928 | 0.23977 | 0.23922 | 0.23835 | 0.23992 | 0.23992 | 0.23992 | 0.23992 | 0.23992 | 0.23992 | 0.23992 | 0.23992 | 0.23992 | 0.23992
| Total |  | 26.0801 |  |  | 1.8078 | 2.1352 | 2.2023 | 1.8666 | 2.1728 | 2.1751 | 1.987 | 1.6683 | 1.5901 | 1.6092 | 1.5646 | 1.611 | 1.622 | 1.6271 | 1.628 | 1.6511 | 1.6511 | 1.6511 | 1.6511 | 1.6511 | 1.6511 | 1.6511 | 1.6511 | 1.6511 | 1.6511
Average Incremental Cost
|  |  |  | AIC 20 | 0 2014/15: Δ MW Total; 1 2015/16: 244.5409; 2 2016/17: 239.1493; 3 2017/18: 233.9055; 4 2018/19: 220.9066; 5 2019/20: 161.1562; 11 2025/26: voltage step
[5 empty] | Δ cost Total | 4.6847 | 6.8181 | 3.4807 | 7.4667 | 3.6299 | 26.0801 |  |  |  |  | increment
[5 empty] | Δ MW | ST | HV bus | HV net | LV bus | LV net | Alloc. | $/kW/year | pf | $/kVA/year |  | $/kW | $/kVA
|  |  |  | ST | 0 2014/15: 5.3916; 1 2015/16: 0.10329; 6 2020/21: 0.10329; 7 2021/22: 19.157; 8 2022/23: 0.95; 9 2023/24: 18.1991; 11 2025/26: 19.157; 12 2026/27: 18.1991
|  |  |  | HV bus | 0 2014/15: 5.2439; 1 2015/16: 0.10046; 2 2016/17: 0.1495; 6 2020/21: 0.24996; 7 2021/22: 47.6667; 8 2022/23: 0.9; 9 2023/24: 42.9; 11 2025/26: 28.5097; 12 2026/27: 25.6587
|  |  |  | HV net | 0 2014/15: 12.9989; 1 2015/16: 0.24902; 2 2016/17: 0.37059; 3 2017/18: 0.19344; 6 2020/21: 0.81305; 7 2021/22: 62.5477; 8 2022/23: 0.9; 9 2023/24: 56.2929; 11 2025/26: 14.881; 12 2026/27: 13.3929
|  |  |  | LV bus | 0 2014/15: 59.7504; 1 2015/16: 1.1446; 2 2016/17: 1.7035; 3 2017/18: 0.88915; 4 2018/19: 2.0196; 6 2020/21: 5.7568; 7 2021/22: 96.3477; 8 2022/23: 0.9; 9 2023/24: 86.713; 11 2025/26: 33.8001; 12 2026/27: 30.4201
|  |  |  | LV net | 0 2014/15: 161.1562; 1 2015/16: 3.0873; 2 2016/17: 4.5945; 3 2017/18: 2.3982; 4 2018/19: 5.4471; 5 2019/20: 3.6299; 6 2020/21: 19.157; 7 2021/22: 118.8721; 8 2022/23: 0.9; 9 2023/24: 106.9849; 11 2025/26: 22.5244; 12 2026/27: 20.2719
[5 empty] | 244.5409 | 4.6847 | 6.8181 | 3.4807 | 7.4667 | 3.6299 | 26.0801
Note on G3: Real Vanilla WACC as per AER final PTRM: Sheet WACC, cell G19. File: AER - SA Power Networks distribution determination - 2016-17 return on debt update - PTRM - June 2016

## Standalone Avoidable
Stand-Alone costs of tariff classes ($M pa)
| 2020/21 | 2020/21 |  |  | Tariff Class |  |  |  |  | Tariff Class
Network Level | Cost Pool | Adj Cost Pool | Major Business | HV Business | Large LV Business | Small Business | Residential | Major Business | HV Business | Large LV Business | Small Business | Residential
Sub-Transmission | 64.3 | 57.87 | 37% | 36% | 48% | 48% | 98% | 21.4119 | 20.8332 | 27.7776 | 27.7776 | 56.7126
Zone Substation | 140.7 | 126.63 | 8% | 11% | 40% | 40% | 86% | 10.1304 | 13.9293 | 50.652 | 50.652 | 108.9018
HV Network | 267.4 | 240.66 | 3% | 7% | 39% | 39% | 92% | 7.2198 | 16.8462 | 93.8574 | 93.8574 | 221.4072
Distribution Transformers | 136.7 | 123.03 |  |  | 32% | 32% | 55% | 0 | 0 | 39.3696 | 39.3696 | 67.6665
LV Networks | 120.6 | 108.54 |  |  |  | 32% | 90% | 0 | 0 | 0 | 34.7328 | 97.686
LV Services | 44.2 | 39.78 |  |  |  | 32% | 90% | 0 | 0 | 0 | 12.7296 | 35.802
Customer Related | 28.1 | 28.1 |  |  | 1% | 10% | 90% | 0 | 0 | 0.281 | 2.81 | 25.29
Non-System Costs |  | 77.39 | 53% | 55% | 73% | 73% | 97% | 41.0167 | 42.5645 | 56.4947 | 56.4947 | 75.0683
| 802 | 802 | [5 empty] | 79.7788 | 94.1732 | 268.4323 | 318.4237 | 688.5344
Avoidable costs of tariff classes ($M pa)
| 2020/21 | 2020/21 |  |  | Tariff Class |  |  |  |  | Tariff Class
Network Level | Cost Pool | Adj Cost Pool | Major Business | HV Business | Large LV Business | Small Business | Residential | Major Business | HV Business | Large LV Business | Small Business | Residential
Sub-Transmission | 64.3 | 57.87 | -1% | -1% | -3% | -3% | -2% | -0.5787 | -0.5787 | -1.7361 | -1.7361 | -1.1574
Zone Substation | 140.7 | 126.63 | -4% | -4% | -4% | -4% | -14% | -5.0652 | -5.0652 | -5.0652 | -5.0652 | -17.7282
HV Network | 267.4 | 240.66 |  |  | -4% | -4% | -22% | 0 | 0 | -9.6264 | -9.6264 | -52.9452
Distribution Transformers | 136.7 | 123.03 |  |  | -23% | -23% | -36% | 0 | 0 | -28.2969 | -28.2969 | -44.2908
LV Networks | 120.6 | 108.54 |  |  |  | -10% | -68% | 0 | 0 | 0 | -10.854 | -73.8072
LV Services | 44.2 | 39.78 |  |  |  | -10% | -68% | 0 | 0 | 0 | -3.978 | -27.0504
Customer Related | 28.1 | 28.1 |  |  | -1% | -10% | -68% | 0 | 0 | -0.281 | -2.81 | -19.108
Non-System Costs |  | 77.39 |  |  | -2% | -2% | -27% | 0 | 0 | -1.5478 | -1.5478 | -20.8953
| 802 | 802 | [5 empty] | -5.6439 | -5.6439 | -46.5534 | -63.9144 | -256.9825