## LOGIC + assumptions
Logic | Assumptions | Consider?
feeder data averages out as there is a sufficient quantatiy of them, new vs old, average out/in cycle
All DD notifications were extracted from SAP from 2009 to today. | 5 years worth of data is sufficient, anything previous was too in accurate, NO CLEANING HAS OCCURED | 2009 2010 2011 has small inspection lengths 1.3k km, 3k km and 5km
All feeder data was extracted from GIS | NO CLEANING HAS OCCURED | cpi, and other escalators, costs/labor
All cycle data was extracted from SAP |  | for the exercise we assume inspections are 100% accurate in reality, this is lower and will drive up all rates by the accuracy margin.
DD Notifications had there GEO ID dumped from Sap, and then GIS cross referenced the locations to provide BRFA and Corrosion zone information. | Defects with BERR and DLFL status were removed, any Priority 4 defects were also removed as they were not actual defects(work markers). | defects that were not assignable to a feeder, do we multiply up the rates?
DD notifcations had their WO lists sumamrizsed and dumped from SAP, these were then used to allocated costs, checks were done to look for multiple notication assignment. |  | SCONRR
DD notifcation costs per defect were allocated from the WO, and flags set for defects with zero costs and not completed |  | LMC 011 lmc 017, lmd 022 are not used
All FM notifications were dumped | Not used due to these being natural occurances, heat waves, storms, cars etc.
The Feeder data and Cycle data was consolidated. | Feeders with Missing data are ignored for calculation purposes
High voltage and Low voltage data was consolidated, Cycles amalgamated and OH lengths summed | defects are not referenced to HV or LV, Cycles for HV and LV were found to be the same for the same feeders
SCONRR data was added to Feeder Data | Feeders with Missing data are ignored for calculation purposes, SCONRR data is a indicator of load rating, for this is gives a basic pole density calculation for urban vs rural infrastructure.
SCONRR data was consolidated in 3 areas, Urban, Rural, No Area | Urban= CBD and urban, Rural = rural short+ rural long, everything else no area, some extra data found from other sources
Fire risk data from GIS was used as main BFRA data. | Prescribed no fire risk was set to no fire risk, NOTE different wording for GIS and SAP
Cycle data was cleaned, to 'Not in cycle' and 'in cycle' | Not in cycle, was set for anything with no data, no record, last inspection cycle was 2014, 2009, 2010m 2011. Upon inspection of data from 2009 and 2010, there was 5000 and 10000 defects found, compared to 14k (2011) 35k(2012) and 22k(2013) with 30k tracking for 2014, these years (2009,2010, 2011) were deemed to be to small for proper use, due to lack of inspections done. Note were there less feeder km inspected in 2009, 2010 and 2011 yes..
Notifications had a feeder assigned from a Floc as the room code was not accurate enough, along with the CZ and BFRA codes, they can now be assiged to a individual feeder | single instance of data copied to feeder sheet, (single instance of feeder data also to notification sheet, in future combine equations into one workbook)
Feeders have counted up their defects, by type, year, total, priority. Also the removal of the 2009, 2010, 2011 and 2014 data was removed for the defect rate calculation. | notification date used to find year
The year of the previous inspection was sourced were possible, to give Years since last inspecton, (YSI) this provided a time interval since the last large amount of work done on the feeder. | A check was done to see if the year matched the previous inspection date in the cycle data AND also removed the date if it was set to 2014. If it was during the defect data set, eg 2012 or 2013 the years since the year of inspection was used, for all other in cycle data not used, and years since the last spection was used, and for all the out of cycle data the date of the last inspection as used, for unknowns or 2014 the average YSI of for CZ 1 and CZ2+3 was used
Correction factor for 2 years of data to bring it up to 5, as we are using 2 years of data with one of them being the main inspecton year, we have 100% +10%. This should then be compared to what should be the 5 year inspection cycle, 100% +10%*4., eg 14/11 | There was found to be a trend of 10% relative to the main inspection year in the other years compared to the main inspection year for an in cycle feeders. Other inspections are occuring throughout the feeders, particularly in the high bushfire risk areas, and other inspections of particular asset types, eg 33kv. | NOT USED see next step
Correction factors for feeders have been applied usign the YSI and the 11/10 coefficient | Note a adjustment of 11/10 to remove the 10% from the second data year. YSI still applies
the defect rates were established looking at a number of variables, corrosion zone, sconrr value, amoutn of defects found and accuracy in feeders for in cycle, the grouped priority defects were used, to help with sample sizes and as prioritys are not a factor of defect rate of occurance. | Using the CZ ratios and Urban/Rural ratios independently of each other, And utilising the defect rate of the largest and most accurate same size (SampleSize*length), Rural CZ2. Following, grouping of defect types was done, with Y/n tag detailing defects that had a correlation to corrosion or urban/rural fectors a average weighting, is teh cases of no positive correlation the individual ratio of the Defect type was utilised.
Once separate rates are determined based off known in cycle feeders, then ratios relative to the different types corrosion and sconrr are developed, the average of these ratios using good data(large sample size) is used, and a basis of CZ2 rural defect rate(largest most accuracte sample size) is used across the defect types. A table is generated giving a overall defect rate, by feeder type, | the ratios are dependent of defect type! For those that are independent of the factors of Corrosion and Urban/Rural, the singular defect ratio for that defect is used. Also there is a assumption that there is always a defect rate regardless of the given data to analyse,
In the notification sheet Averege cost rates were extracted with the states, SCONRR, VOLTAGE, Defect type. | (this to be moved to the Feeder sheet)
Also small data sets for rates were extracted, defect type and voltage, defect type and SCONRR
Once separate cost rates are determined based off known in cycle feeders, then ratios relative to the different types voltage and sconrr are developed, the average of these ratios using good data(large sample size) is used, and a basis of 11KV rural defect rate(large sample size) is used across the defect types. A table is generated giving a overall defect cost rate, by feeder type, which is fed into the 'backlog calculation' | 11kv is the same as 7.6kv, as they are phasing out 7.6kv with 11kv equipment, the ratios are not independent of defect type! Also there is a assumption that there is always a cost rate regardless of the given data to analyse
The consolidated feeder information now takes the modeled defect rate and generates the defects of the individual feeders, taking into account the length of the feeders and the YSI to give a total number of defects occuring in 2014
For Steady state over 5 years, a YSI of 5years is set, | NB inspection schedule needs to be considered now.
Note on A7: BIRDT0: pre 2009??
Note on A19: BIRDT0: this could have been applied to the length or defect rate for the final calculation, i chose the length