## CONFIG
VCR
Customer Type | Aggregate (%) | VCR ($/kWh) | VCR ($/MWh)
Residential | 36.9% | 26.88 | 26880
Commercial | 44.8% | 44.72 | 44720
Industrial (non D/C) | 16.3% | 44.06 | 44060
Agricultural | 2% | 47.67 | 47670
Financial Year | CPI | Annual (%) | Cumulative (%)
2015 | 105.4 |  | 1
2016 | 108.2 | 1.0266 | 1.0266
2017 | 110.5 | 1.0213 | 1.0484
2018 | 112.6 | 1.019 | 1.0683
2019 | 114.1 | 1.0133 | 1.0825
Year | METRO_STH_MW | GROWTH
2029 | 660.6451
2030 | 658.997 | 0.99751
2031 | 657.3735 | 0.99754
2032 | 655.7808 | 0.99758
2033 | 654.2428 | 0.99765
2034 | 652.7383 | 0.9977
2035 | 651.2545 | 0.99773
2036 | 649.8734 | 0.99788
2037 | 648.4307 | 0.99778
2038 | 647.0109 | 0.99781
2039 | 645.5993 | 0.99782
| AVG: | 0.9977
| LINE | SUB | GEN
Plant Life (yrs) | 55 | 45 | 20
Depreciation (p.a.) | 1.818% | 2.222% | 5%
Ops & Maint (p.a.) | 1.5% | 1.5% | 1.5%
Sensitivity (+/-)
VCR | 30%
Load Factor | 30%
Reliability | 30%
Costs | 30%
Discount Rate | 25%
Reliability | Outages/km/yr
Re-Insulation | 0.01

## INPUTS
REGULATORY ANALYSIS
Start Year: |  | 2023
Duration: | yrs | 10
Insolation: | 0.68 or 1.00 | 1
Losses: | Y/N | Y
SENSITIVITY
WACC/Discount Rate: | % | 0.03507
VCR
Year: |  | 2019
VCR: | $/MWh | 29098.7476
Residential | % | 100%
Commercial | % | 0%
Industrial (non D/C) | % | 0%
Agricultural | % | 0%
RELIABILITY - LINE
Overhead: | Outages/km/yr | 0.015
Outage Duration: | hrs | 8
RELIABILITY - SUBSTATION
Transformer: | Outages/yr | 0.02
TF Restoration: | hrs | 2
Feeder Transfers: | hrs | 4
Mobile Substation: | hrs | 24
TF Replacement: | hrs | 168
GENERATION
Capacity | MW | 8
Deployment Time: | hh:mm | 0:30
Status | Y/N | Y

## FORECASTS
INCLUDE | FORECAST (MW) | SD1570 | SD1568 | SD1569 | KI | SHWF | MYPO
Y | 2019 | 49.7426 | 23.3001 | 17.2725 | 6.5986 | 8.7699 | 6.0275
Y | 2020 | 40.4827 | 19.8351 | 13.5668 | 5.6402 | 7.5551 | 6.2682
Y | 2021 | 40.3923 | 19.8792 | 13.5052 | 5.5759 | 7.4812 | 6.374
Y | 2022 | 40.2946 | 19.919 | 13.4441 | 5.5115 | 7.4075 | 6.4749
Y | 2023 | 40.0722 | 19.9177 | 13.3665 | 5.4313 | 7.3155 | 6.5512
Y | 2024 | 39.8211 | 19.9055 | 13.2866 | 5.3475 | 7.2204 | 6.6189
Y | 2025 | 39.6493 | 19.917 | 13.2197 | 5.2754 | 7.1391 | 6.6972
Y | 2026 | 39.481 | 19.9285 | 13.1545 | 5.205 | 7.0593 | 6.774
Y | 2027 | 39.3167 | 19.9403 | 13.0911 | 5.136 | 6.9811 | 6.8493
Y | 2028 | 39.1561 | 19.9524 | 13.0293 | 5.0684 | 6.9044 | 6.9231
Y | 2029 | 38.9999 | 19.9652 | 12.9691 | 5.0027 | 6.8292 | 6.9962
Y | 2030 | 38.9102 | 19.9193 | 12.9392 | 4.9911 | 6.8135 | 6.9801
Y | 2031 | 38.8206 | 19.8734 | 12.9094 | 4.9797 | 6.7978 | 6.964
Y | 2032 | 38.7313 | 19.8277 | 12.8797 | 4.9682 | 6.7821 | 6.948
Y | 2033 | 38.6422 | 19.7821 | 12.8501 | 4.9568 | 6.7665 | 6.932
N | 2034 | 38.5532 | 19.7366 | 12.8205 | 4.9454 | 6.751 | 6.916
N | 2035 | 38.4645 | 19.6911 | 12.791 | 4.934 | 6.7354 | 6.9001
N | 2036 | 38.376 | 19.6458 | 12.7616 | 4.9226 | 6.7199 | 6.8842
N | 2037 | 38.2877 | 19.6006 | 12.7322 | 4.9113 | 6.7045 | 6.8684
N | 2038 | 38.1996 | 19.5555 | 12.7029 | 4.9 | 6.689 | 6.8526
N | 2039 | 38.1117 | 19.5105 | 12.6737 | 4.8887 | 6.6736 | 6.8368
N | 2040 | 38.024 | 19.4656 | 12.6445 | 4.8775 | 6.6583 | 6.8211
N | 2041 | 37.9365 | 19.4208 | 12.6154 | 4.8662 | 6.643 | 6.8054
N | 2042 | 37.8492 | 19.3761 | 12.5864 | 4.855 | 6.6277 | 6.7897
N | 2043 | 37.7621 | 19.3315 | 12.5574 | 4.8439 | 6.6124 | 6.7741
N | 2044 | 37.6752 | 19.2871 | 12.5285 | 4.8327 | 6.5972 | 6.7585

## LDC
| SD1570 |  | SD1568 |  | SD1569 |  | TOTAL
INSOL (MAX): | 0.68 | 1 | 0.68 | 1 | 0.68 | 1 | 0.68 | 1
PEAK: | 57.5585 | 59.337 | 26.8146 | 28.6547 | 25.2411 | 26.6405 | 81.4387 | 84.6635
AVG: | 18.0483 | 19.9195 | 10.425 | 11.1612 | 8.1428 | 8.6824 | 28.2291 | 30.8486
LF: | 0.31357 | 0.3357 | 0.38878 | 0.38951 | 0.3226 | 0.32591 | 0.34663 | 0.36437
LLF: | 0.10717 | 0.12265 | 0.15759 | 0.15871 | 0.10827 | 0.11087 | 0.12759 | 0.14134
HRS: | 7324 | 7324 | 7323.5 | 7323.5 | 7323.5 | 7323.5 | 7323.5 | 7323.5
LOAD_% | TIME_% | TIME_% | TIME_% | TIME_% | TIME_% | TIME_% | TIME_% | TIME_%
0.01 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
0.02 | 1 | 1 | 0.99863 | 0.99863 | 1 | 1 | 1 | 1
0.03 | 1 | 1 | 0.99843 | 0.99843 | 0.99966 | 0.9998 | 1 | 1
0.04 | 1 | 1 | 0.99809 | 0.99822 | 0.99932 | 0.99952 | 1 | 1
0.05 | 1 | 1 | 0.99782 | 0.99788 | 0.99911 | 0.99925 | 1 | 1
0.06 | 1 | 1 | 0.99747 | 0.99761 | 0.9985 | 0.99904 | 1 | 1
0.07 | 1 | 1 | 0.99727 | 0.9972 | 0.99809 | 0.99843 | 1 | 1
0.08 | 1 | 1 | 0.99672 | 0.99679 | 0.99734 | 0.99816 | 1 | 1
0.09 | 1 | 1 | 0.99638 | 0.99652 | 0.99679 | 0.99782 | 1 | 1
0.1 | 1 | 1 | 0.99556 | 0.9959 | 0.99604 | 0.99686 | 1 | 1
0.11 | 1 | 1 | 0.99536 | 0.9957 | 0.99474 | 0.99556 | 1 | 1
0.12 | 1 | 1 | 0.99481 | 0.99522 | 0.99338 | 0.99427 | 1 | 1
0.13 | 1 | 1 | 0.9942 | 0.99481 | 0.99208 | 0.99297 | 1 | 1
0.14 | 0.99993 | 1 | 0.99351 | 0.9944 | 0.99065 | 0.99222 | 1 | 1
0.15 | 0.99993 | 1 | 0.9931 | 0.99413 | 0.98962 | 0.99037 | 1 | 1
0.16 | 0.9998 | 0.99406 | 0.99229 | 0.99351 | 0.98757 | 0.98867 | 1 | 1
0.17 | 0.99194 | 0.99358 | 0.99188 | 0.99297 | 0.98573 | 0.98635 | 1 | 1
0.18 | 0.98826 | 0.99324 | 0.99119 | 0.99283 | 0.98348 | 0.98341 | 0.9998 | 0.9998
0.19 | 0.98191 | 0.99017 | 0.99044 | 0.99194 | 0.98006 | 0.98 | 0.99959 | 0.99379
0.2 | 0.96894 | 0.97918 | 0.98887 | 0.99119 | 0.97638 | 0.97726 | 0.9931 | 0.99331
0.21 | 0.93958 | 0.95371 | 0.98805 | 0.99037 | 0.97351 | 0.97488 | 0.99126 | 0.99297
0.22 | 0.9004 | 0.92886 | 0.98751 | 0.98976 | 0.97023 | 0.97064 | 0.98757 | 0.99153
0.23 | 0.85978 | 0.89671 | 0.98682 | 0.98921 | 0.96443 | 0.966 | 0.97897 | 0.98484
0.24 | 0.80837 | 0.86121 | 0.98573 | 0.98191 | 0.95658 | 0.95521 | 0.963 | 0.96914
0.25 | 0.7586 | 0.82387 | 0.98416 | 0.97965 | 0.94026 | 0.93937 | 0.93337 | 0.94347
0.26 | 0.71109 | 0.78768 | 0.9761 | 0.97658 | 0.91514 | 0.91322 | 0.8965 | 0.91561
0.27 | 0.66159 | 0.75177 | 0.97133 | 0.9703 | 0.8782 | 0.87363 | 0.85308 | 0.88462
0.28 | 0.61783 | 0.70979 | 0.96491 | 0.96136 | 0.82515 | 0.82857 | 0.80849 | 0.85232
0.29 | 0.56902 | 0.66671 | 0.95282 | 0.94722 | 0.76862 | 0.77524 | 0.76132 | 0.81211
0.3 | 0.52574 | 0.62541 | 0.93282 | 0.92545 | 0.70888 | 0.71462 | 0.70991 | 0.77326
0.31 | 0.4817 | 0.58616 | 0.90763 | 0.89875 | 0.64006 | 0.64812 | 0.65863 | 0.73373
0.32 | 0.44054 | 0.54697 | 0.87417 | 0.86564 | 0.57411 | 0.57718 | 0.61344 | 0.69045
0.33 | 0.40197 | 0.50758 | 0.83471 | 0.82925 | 0.50345 | 0.51164 | 0.56646 | 0.64566
0.34 | 0.36599 | 0.46928 | 0.79088 | 0.78712 | 0.43333 | 0.44268 | 0.51997 | 0.59807
0.35 | 0.33069 | 0.43146 | 0.74363 | 0.73947 | 0.36663 | 0.38247 | 0.46999 | 0.55704
0.36 | 0.29731 | 0.39746 | 0.69345 | 0.68908 | 0.30177 | 0.32799 | 0.42473 | 0.51335
0.37 | 0.27055 | 0.36298 | 0.6432 | 0.63194 | 0.24811 | 0.27651 | 0.38056 | 0.47102
0.38 | 0.24488 | 0.32803 | 0.58722 | 0.57275 | 0.20325 | 0.23063 | 0.34068 | 0.43101
0.39 | 0.22023 | 0.29854 | 0.53171 | 0.51744 | 0.16249 | 0.18441 | 0.30443 | 0.39312
0.4 | 0.19661 | 0.26946 | 0.47279 | 0.46166 | 0.1291 | 0.14508 | 0.27036 | 0.35331
0.41 | 0.17374 | 0.24324 | 0.41421 | 0.40937 | 0.097904 | 0.11361 | 0.24066 | 0.31624
0.42 | 0.15545 | 0.21989 | 0.36103 | 0.36007 | 0.073394 | 0.087868 | 0.21247 | 0.28204
0.43 | 0.13804 | 0.19573 | 0.31126 | 0.31297 | 0.055097 | 0.069161 | 0.18475 | 0.25343
0.44 | 0.12118 | 0.17327 | 0.26565 | 0.27262 | 0.041101 | 0.053117 | 0.16304 | 0.22448
0.45 | 0.10609 | 0.1504 | 0.22121 | 0.23172 | 0.030586 | 0.040759 | 0.14255 | 0.1982
0.46 | 0.090456 | 0.13039 | 0.18604 | 0.19308 | 0.022257 | 0.032976 | 0.12351 | 0.17219
0.47 | 0.079055 | 0.11292 | 0.15587 | 0.16044 | 0.01741 | 0.027651 | 0.10746 | 0.14638
0.48 | 0.067381 | 0.099945 | 0.12856 | 0.13395 | 0.013791 | 0.022394 | 0.091555 | 0.12596
0.49 | 0.058575 | 0.086155 | 0.10255 | 0.11129 | 0.011538 | 0.018434 | 0.077559 | 0.10753
0.5 | 0.050246 | 0.074276 | 0.084522 | 0.092442 | 0.0097631 | 0.015362 | 0.065065 | 0.091623
0.51 | 0.043419 | 0.063695 | 0.069434 | 0.076193 | 0.0077832 | 0.013655 | 0.05455 | 0.078583
0.52 | 0.036729 | 0.053591 | 0.056326 | 0.062538 | 0.0065542 | 0.012357 | 0.04547 | 0.067181
0.53 | 0.030653 | 0.045126 | 0.046016 | 0.051273 | 0.0055301 | 0.01106 | 0.038233 | 0.054687
0.54 | 0.025259 | 0.036933 | 0.036595 | 0.043149 | 0.0051888 | 0.00949 | 0.031474 | 0.045743
0.55 | 0.020754 | 0.029833 | 0.028675 | 0.035434 | 0.0045743 | 0.0082611 | 0.024647 | 0.037755
0.56 | 0.015907 | 0.024986 | 0.023418 | 0.030518 | 0.0040964 | 0.0070322 | 0.01939 | 0.031064
0.57 | 0.013449 | 0.02089 | 0.01898 | 0.02649 | 0.003755 | 0.0058032 | 0.015908 | 0.024988
0.58 | 0.010855 | 0.016794 | 0.017137 | 0.024169 | 0.0033454 | 0.0046426 | 0.012221 | 0.020619
0.59 | 0.0088749 | 0.013654 | 0.014815 | 0.021438 | 0.0028675 | 0.0042329 | 0.0095583 | 0.017
0.6 | 0.0078509 | 0.011537 | 0.012972 | 0.020209 | 0.0026627 | 0.003755 | 0.0076466 | 0.014201
0.61 | 0.0064855 | 0.010104 | 0.01188 | 0.017273 | 0.0025944 | 0.0034137 | 0.0062129 | 0.012426
0.62 | 0.0056663 | 0.0088749 | 0.01106 | 0.015566 | 0.0023896 | 0.0029358 | 0.0053253 | 0.01106
0.63 | 0.0049836 | 0.008124 | 0.0098314 | 0.014474 | 0.0021165 | 0.0027309 | 0.0045743 | 0.0099679
0.64 | 0.0044375 | 0.0070999 | 0.0088073 | 0.01304 | 0.0017751 | 0.0023213 | 0.0040281 | 0.0088755
0.65 | 0.0040279 | 0.0064855 | 0.0073735 | 0.011333 | 0.0015703 | 0.0021165 | 0.003755 | 0.0078514
0.66 | 0.003823 | 0.0060076 | 0.0066225 | 0.010378 | 0.0015703 | 0.0017068 | 0.0035502 | 0.0073735
0.67 | 0.0034817 | 0.005325 | 0.0058032 | 0.0088755 | 0.0012289 | 0.001502 | 0.0031406 | 0.0062811
0.68 | 0.0031404 | 0.0047788 | 0.0051888 | 0.0083976 | 0.0010241 | 0.0013655 | 0.0028675 | 0.0056667
0.69 | 0.0030721 | 0.0044375 | 0.0049157 | 0.0075101 | 0.00081928 | 0.0010241 | 0.0026627 | 0.0051888
0.7 | 0.0025942 | 0.0040961 | 0.0041647 | 0.0065542 | 0.00054619 | 0.00075101 | 0.0025944 | 0.0048474
0.71 | 0.0023211 | 0.0037548 | 0.0038916 | 0.0055984 | 0.00047791 | 0.00047791 | 0.0024578 | 0.0043695
0.72 | 0.0019798 | 0.0034134 | 0.0034819 | 0.0047791 | 0.00047791 | 0.00034137 | 0.0023213 | 0.0038233
0.73 | 0.0017067 | 0.0030038 | 0.0030723 | 0.0039599 | 0.00027309 | 0.00020482 | 0.0021165 | 0.0035502
0.74 | 0.0017067 | 0.002799 | 0.0029358 | 0.0035502 | 0.00020482 | 0.00020482 | 0.0021165 | 0.0033454
0.75 | 0.0015019 | 0.0023894 | 0.0026627 | 0.0032771 | 0.00013655 | 0.00013655 | 0.0019117 | 0.0030723
0.76 | 0.0014336 | 0.0023211 | 0.0025261 | 0.0030723 | 0.00013655 | 6.8273e-05 | 0.0016386 | 0.0027992
0.77 | 0.0012971 | 0.0021846 | 0.0023213 | 0.0026627 | 0.00013655 | 6.8273e-05 | 0.001502 | 0.0024578
0.78 | 0.0011606 | 0.0019115 | 0.0020482 | 0.0023896 | 0.00013655 | 6.8273e-05 | 0.0012289 | 0.002253
0.79 | 0.0011606 | 0.0016384 | 0.0019117 | 0.002253 | 0.00013655 | 6.8273e-05 | 0.0012289 | 0.0020482
0.8 | 0.0010923 | 0.0016384 | 0.0019117 | 0.0019799 | 6.8273e-05 | 6.8273e-05 | 0.0011606 | 0.0018434
0.81 | 0.00095576 | 0.0015019 | 0.0018434 | 0.001502 | 6.8273e-05 | 6.8273e-05 | 0.0011606 | 0.0015703
0.82 | 0.00095576 | 0.0014336 | 0.0014337 | 0.0012972 | 6.8273e-05 | 6.8273e-05 | 0.0011606 | 0.001502
0.83 | 0.00088749 | 0.0013654 | 0.0012289 | 0.0011606 | 6.8273e-05 | 6.8273e-05 | 0.0010241 | 0.001502
0.84 | 0.00081922 | 0.0012971 | 0.0010924 | 0.0010924 | 6.8273e-05 | 6.8273e-05 | 0.0010241 | 0.0014337
0.85 | 0.00081922 | 0.0012971 | 0.0010241 | 0.00095583 | 6.8273e-05 | 6.8273e-05 | 0.00095583 | 0.0014337
0.86 | 0.00068269 | 0.0012971 | 0.00068273 | 0.00095583 | 6.8273e-05 | 6.8273e-05 | 0.00088755 | 0.0012972
0.87 | 0.00061442 | 0.0011606 | 0.00061446 | 0.00068273 | 6.8273e-05 | 6.8273e-05 | 0.00081928 | 0.0012289
0.88 | 0.00061442 | 0.0010923 | 0.00054619 | 0.00054619 | 6.8273e-05 | 6.8273e-05 | 0.00075101 | 0.0011606
0.89 | 0.00054615 | 0.0010923 | 0.00047791 | 0.00047791 | 6.8273e-05 | 6.8273e-05 | 0.00068273 | 0.0011606
0.9 | 0.00054615 | 0.00095576 | 0.00040964 | 0.00020482 | 6.8273e-05 | 6.8273e-05 | 0.00061446 | 0.0010924
0.91 | 0.00054615 | 0.00095576 | 0.00034137 | 0.00013655 | 6.8273e-05 | 6.8273e-05 | 0.00054619 | 0.00095583
0.92 | 0.00047788 | 0.00095576 | 0.00027309 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00054619 | 0.00095583
0.93 | 0.00034134 | 0.00075096 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00054619 | 0.00095583
0.94 | 0.00034134 | 0.00061442 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00047791 | 0.00088755
0.95 | 0.00034134 | 0.00034134 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00040964 | 0.00075101
0.96 | 0.00034134 | 0.00034134 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00034137 | 0.00054619
0.97 | 0.00020481 | 0.00013654 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00034137 | 0.00027309
0.98 | 0.00020481 | 0.00013654 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00027309 | 0.00013655
0.99 | 0.00013654 | 0.00013654 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00020482 | 0.00013655
1 | 6.8269e-05 | 6.8269e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 6.8273e-05 | 0.00020482 | 6.8273e-05

## BASE
|  | LINE | UNITS | SD1570 | SD1568 | SD1569
|  | Length | km | 15.317 | 16.558 | 17.063
|  | Outage | yr/len | 0.22975 | 0.24837 | 0.25594
|  | Outage Duration | hrs | 8 | 7.5 | 7.5
|  | Outage | hrs/yr/len | 1.838 | 1.8628 | 1.9196
|  | Gen | Y/N | - | Y | Y
|  | Gen Resp Time | hrs | - | 0.5 | 0.5
|  | Load Factor: |  | 0.3357 | 0.38951 | 0.32591
|  | LLF: |  | 0.12265 | 0.15871 | 0.11087
|  |  |  | FORECAST LOAD (MW) |  |  |  | ENERGY @ RISK (MWh) | [5 empty] | LOAD SENSITIVITY |  |  | RISK VALUE ($M)
YEAR | INCLUDE |  |  | SD1570 | SD1568 | SD1569 | KI | SD1570 | SD1568_PRE-KIGEN | SD1568_POST-KIGEN | SD1568 | TOTAL | LF VARIANCE (%): | -30% | 30% | VCR ($/MWh): | 20369.1233 | 29098.7476 | 37828.3719
2019 | N |  |  | 49.7426 | 23.3001 | 17.2725 | 6.5986 | 26.9284 | 0.94817 | 10.1947 | 11.1429 | 38.0713 |  | 26.6499 | 49.4927 |  | 0 | 0 | 0
2020 | N |  |  | 40.4827 | 19.8351 | 13.5668 | 5.6402 | 21.9155 | 0.80717 | 8.6647 | 9.4718 | 31.3873 |  | 21.9711 | 40.8035 |  | 0 | 0 | 0
2021 | N |  |  | 40.3923 | 19.8792 | 13.5052 | 5.5759 | 21.8666 | 0.80896 | 8.7308 | 9.5398 | 31.4064 |  | 21.9845 | 40.8283 |  | 0 | 0 | 0
2022 | N |  |  | 40.2946 | 19.919 | 13.4441 | 5.5115 | 21.8137 | 0.81058 | 8.7945 | 9.6051 | 31.4187 |  | 21.9931 | 40.8443 |  | 0 | 0 | 0
2023 | Y |  |  | 40.0722 | 19.9177 | 13.3665 | 5.4313 | 21.6933 | 0.81053 | 8.8426 | 9.6532 | 31.3464 |  | 21.9425 | 40.7504 |  | 638499.418 | 912142.0257 | 1185784.6334
2024 | Y |  |  | 39.8211 | 19.9055 | 13.2866 | 5.3475 | 21.5573 | 0.81004 | 8.8864 | 9.6964 | 31.2537 |  | 21.8776 | 40.6298 |  | 636611.0097 | 909444.2996 | 1182277.5895
2025 | Y |  |  | 39.6493 | 19.917 | 13.2197 | 5.2754 | 21.4643 | 0.8105 | 8.9373 | 9.7478 | 31.2121 |  | 21.8485 | 40.5758 |  | 635763.8766 | 908234.1095 | 1180704.3423
2026 | Y |  |  | 39.481 | 19.9285 | 13.1545 | 5.205 | 21.3732 | 0.81097 | 8.9874 | 9.7984 | 31.1716 |  | 21.8201 | 40.5231 |  | 634938.7215 | 907055.3164 | 1179171.9114
2027 | Y |  |  | 39.3167 | 19.9403 | 13.0911 | 5.136 | 21.2842 | 0.81145 | 9.0367 | 9.8482 | 31.1324 |  | 21.7927 | 40.4722 |  | 634140.4002 | 905914.8574 | 1177689.3147
2028 | Y |  |  | 39.1561 | 19.9524 | 13.0293 | 5.0684 | 21.1973 | 0.81194 | 9.0853 | 9.8973 | 31.0946 |  | 21.7662 | 40.423 |  | 633369.3493 | 904813.3561 | 1176257.3629
2029 | Y |  |  | 38.9999 | 19.9652 | 12.9691 | 5.0027 | 21.1128 | 0.81246 | 9.1333 | 9.9458 | 31.0585 |  | 21.741 | 40.3761 |  | 632635.0348 | 903764.3355 | 1174893.6361
2030 | Y |  |  | 38.9102 | 19.9193 | 12.9392 | 4.9911 | 21.0642 | 0.81059 | 9.1123 | 9.9229 | 30.9871 |  | 21.6909 | 40.2832 |  | 631179.2668 | 901684.6668 | 1172190.0669
2031 | Y |  |  | 38.8206 | 19.8734 | 12.9094 | 4.9797 | 21.0157 | 0.80873 | 9.0913 | 9.9 | 30.9158 |  | 21.641 | 40.1905 |  | 629726.8486 | 899609.7837 | 1169492.7188
2032 | Y |  |  | 38.7313 | 19.8277 | 12.8797 | 4.9682 | 20.9674 | 0.80687 | 9.0704 | 9.8773 | 30.8446 |  | 21.5912 | 40.098 |  | 628277.7726 | 897539.6752 | 1166801.5777
2033 | Y |  |  | 38.6422 | 19.7821 | 12.8501 | 4.9568 | 20.9191 | 0.80501 | 9.0495 | 9.8545 | 30.7736 |  | 21.5415 | 40.0057 |  | 626832.0311 | 895474.3302 | 1164116.6292
2034 | N |  |  | 38.5532 | 19.7366 | 12.8205 | 4.9454 | 20.871 | 0.80316 | 9.0287 | 9.8319 | 30.7028 |  | 21.492 | 39.9137 |  | 0 | 0 | 0
2035 | N |  |  | 38.4645 | 19.6911 | 12.791 | 4.934 | 20.8229 | 0.80131 | 9.0079 | 9.8092 | 30.6322 |  | 21.4425 | 39.8218 |  | 0 | 0 | 0
2036 | N |  |  | 38.376 | 19.6458 | 12.7616 | 4.9226 | 20.775 | 0.79947 | 8.9872 | 9.7867 | 30.5617 |  | 21.3932 | 39.7302 |  | 0 | 0 | 0
2037 | N |  |  | 38.2877 | 19.6006 | 12.7322 | 4.9113 | 20.7272 | 0.79763 | 8.9665 | 9.7641 | 30.4914 |  | 21.344 | 39.6388 |  | 0 | 0 | 0
2038 | N |  |  | 38.1996 | 19.5555 | 12.7029 | 4.9 | 20.6795 | 0.79579 | 8.9459 | 9.7417 | 30.4212 |  | 21.2948 | 39.5476 |  | 0 | 0 | 0
2039 | N |  |  | 38.1117 | 19.5105 | 12.6737 | 4.8887 | 20.6319 | 0.79396 | 8.9253 | 9.7192 | 30.3512 |  | 21.2458 | 39.4565 |  | 0 | 0 | 0
2040 | N |  |  | 38.024 | 19.4656 | 12.6445 | 4.8775 | 20.5845 | 0.79213 | 8.9047 | 9.6969 | 30.2814 |  | 21.1969 | 39.3658 |  | 0 | 0 | 0
2041 | N |  |  | 37.9365 | 19.4208 | 12.6154 | 4.8662 | 20.5371 | 0.79031 | 8.8843 | 9.6746 | 30.2117 |  | 21.1482 | 39.2752 |  | 0 | 0 | 0
2042 | N |  |  | 37.8492 | 19.3761 | 12.5864 | 4.855 | 20.4898 | 0.78849 | 8.8638 | 9.6523 | 30.1421 |  | 21.0995 | 39.1848 |  | 0 | 0 | 0
2043 | N |  |  | 37.7621 | 19.3315 | 12.5574 | 4.8439 | 20.4427 | 0.78668 | 8.8434 | 9.6301 | 30.0728 |  | 21.051 | 39.0946 |  | 0 | 0 | 0
2044 | N |  |  | 37.6752 | 19.2871 | 12.5285 | 4.8327 | 20.3957 | 0.78487 | 8.8231 | 9.6079 | 30.0036 |  | 21.0025 | 39.0047 |  | 0 | 0 | 0
[16 empty] | TOTAL: | 6961973.7293 | 9945676.7561 | 12929379.7829

## OPTION1
CAPEX | [6 empty] | CAPEX SUMMARY |  |  |  | ACCRUED |  |  |  | DEPRECIATION |  |  |  | OPS & MAINTENANCE |  |  |  | COST SUMMARY |  |  |  |  | SENSITIVITY |  |  | RISK VALUE ($)
YEAR | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | YEAR | INCLUDE | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | COST VARIANCE (%): | -30% | 30% | VCR ($/MWh): | 20369.1233 | 29098.7476 | 37828.3719
2023 | 3000000 | 1000000 |  | 4000000 | 2019 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
2024 | 4875000 | 1625000 |  | 6500000 | 2020 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
2025 | 7870500 | 2623500 |  | 10494000 | 2021 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2022 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2023 | Y | 3000000 | 1000000 | 0 | 4000000 | 3000000 | 1000000 | 0 | 4000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 638499.418 | 912142.0257 | 1185784.6334
[5 empty] | 2024 | Y | 4875000 | 1625000 | 0 | 6500000 | 7875000 | 2625000 | 0 | 10500000 | 54545.4545 | 22222.2222 | 0 | 76767.6768 | 45000 | 15000 | 0 | 60000 | 99545.4545 | 37222.2222 | 0 | 136767.6768 |  | 95737.3737 | 177797.9798 |  | 636611.0097 | 909444.2996 | 1182277.5895
[5 empty] | 2025 | Y | 7870500 | 2623500 | 0 | 10494000 | 15745500 | 5248500 | 0 | 20994000 | 143181.8182 | 58333.3333 | 0 | 201515.1515 | 118125 | 39375 | 0 | 157500 | 261306.8182 | 97708.3333 | 0 | 359015.1515 |  | 251310.6061 | 466719.697 |  | 635763.8766 | 908234.1095 | 1180704.3423
[5 empty] | 2026 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2027 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2028 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2029 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2030 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2031 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2032 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2033 | Y | 0 | 0 | 0 | 0 | 15745500 | 5248500 | 0 | 20994000 | 286281.8182 | 116633.3333 | 0 | 402915.1515 | 236182.5 | 78727.5 | 0 | 314910 | 522464.3182 | 195360.8333 | 0 | 717825.1515 |  | 502477.6061 | 933172.697 |  | 0 | 0 | 0
[5 empty] | 2034 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2035 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2036 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2037 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2038 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2039 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2040 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2041 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2042 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2043 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2044 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
TOTAL: | 15745500 | 5248500 | 0 | 20994000 |  |  | 15745500 | 5248500 | 0 | 20994000 |  |  |  |  | 2487981.8182 | 1013622.2222 | 0 | 3501604.0404 | 2052585 | 684195 | 0 | 2736780 | 4540566.8182 | 1697817.2222 | 0 | 6238384.0404 |  | 4366868.8283 | 8109899.2525 |  | 1910874.3043 | 2729820.4348 | 3548766.5652

## OPTION2
CAPEX | [6 empty] | CAPEX SUMMARY |  |  |  | ACCRUED |  |  |  | DEPRECIATION |  |  |  | OPS & MAINTENANCE |  |  |  | COST SUMMARY |  |  |  |  | SENSITIVITY |  |  | RISK VALUE ($)
YEAR | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | YEAR | INCLUDE | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | COST VARIANCE (%): | -30% | 30% | VCR ($/MWh): | 20369.1233 | 29098.7476 | 37828.3719
|  |  |  | 0 | 2019 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
2023 | 5353972 |  |  | 5353972 | 2020 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 2021 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2022 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2023 | Y | 5353972 | 0 | 0 | 5353972 | 5353972 | 0 | 0 | 5353972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 638499.418 | 912142.0257 | 1185784.6334
[5 empty] | 2024 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 424407.3398 | 606296.1998 | 788185.0597
[5 empty] | 2025 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 423842.5844 | 605489.4063 | 787136.2282
[5 empty] | 2026 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 423292.481 | 604703.5443 | 786114.6076
[5 empty] | 2027 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 422760.2668 | 603943.2383 | 785126.2098
[5 empty] | 2028 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 422246.2328 | 603208.9041 | 784171.5753
[5 empty] | 2029 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 421756.6899 | 602509.557 | 783262.4241
[5 empty] | 2030 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 420786.1779 | 601123.1112 | 781460.0446
[5 empty] | 2031 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 419817.8991 | 599739.8558 | 779661.8126
[5 empty] | 2032 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 418851.8484 | 598359.7834 | 777867.7185
[5 empty] | 2033 | Y | 0 | 0 | 0 | 0 | 5353972 | 0 | 0 | 5353972 | 97344.9455 | 0 | 0 | 97344.9455 | 80309.58 | 0 | 0 | 80309.58 | 177654.5255 | 0 | 0 | 177654.5255 |  | 124358.1678 | 230950.8831 |  | 417888.0208 | 596982.8868 | 776077.7528
[5 empty] | 2034 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2035 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2036 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2037 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2038 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2039 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2040 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2041 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2042 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2043 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2044 | N | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
TOTAL: | 5353972 | 0 | 0 | 5353972 |  |  | 5353972 | 0 | 0 | 5353972 |  |  |  |  | 973449.4545 | 0 | 0 | 973449.4545 | 803095.8 | 0 | 0 | 803095.8 | 1776545.2545 | 0 | 0 | 1776545.2545 |  | 1243581.6782 | 2309508.8309 |  | 4854148.9588 | 6934498.5126 | 9014848.0664

## OPTION3
CAPEX | [6 empty] | LOAD RECOVERY | CAPEX SUMMARY |  |  |  | ACCRUED |  |  |  | DEPRECIATION |  |  |  | OPS & MAINTENANCE |  |  |  | COST SUMMARY |  |  |  |  | SENSITIVITY |  |  | RISK VALUE ($)
YEAR | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | YEAR | INCLUDE | SHWF | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | LINE_$ | SUB_$ | GEN_$ | TOTAL_$ | COST VARIANCE (%): | -30% | 30% | VCR ($/MWh): | 20369.1233 | 29098.7476 | 37828.3719
|  |  |  | 0 | 2019 | N | 8.7699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
2023 |  | 3000000 |  | 3000000 | 2020 | N | 7.5551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 2021 | N | 7.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2022 | N | 7.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2023 | Y | 7.3155 | 0 | 3000000 | 0 | 3000000 | 0 | 3000000 | 0 | 3000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 547542.5676 | 782203.668 | 1016864.7684
[5 empty] | 2024 | Y | 7.2204 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 546835.9656 | 781194.2366 | 1015552.5076
[5 empty] | 2025 | Y | 7.1391 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 547000.2078 | 781428.8683 | 1015857.5288
[5 empty] | 2026 | Y | 7.0593 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 547166.9585 | 781667.0835 | 1016167.2086
[5 empty] | 2027 | Y | 6.9811 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 547341.077 | 781915.8243 | 1016490.5716
[5 empty] | 2028 | Y | 6.9044 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 547523.4709 | 782176.387 | 1016829.3031
[5 empty] | 2029 | Y | 6.8292 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 547724.4101 | 782463.443 | 1017202.4759
[5 empty] | 2030 | Y | 6.8135 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 546464.0314 | 780662.902 | 1014861.7726
[5 empty] | 2031 | Y | 6.7978 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 545206.553 | 778866.5043 | 1012526.4556
[5 empty] | 2032 | Y | 6.7821 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 543951.9682 | 777074.2403 | 1010196.5124
[5 empty] | 2033 | Y | 6.7665 | 0 | 0 | 0 | 0 | 0 | 3000000 | 0 | 3000000 | 0 | 66666.6667 | 0 | 66666.6667 | 0 | 45000 | 0 | 45000 | 0 | 111666.6667 | 0 | 111666.6667 |  | 78166.6667 | 145166.6667 |  | 542700.2704 | 775286.1006 | 1007871.9307
[5 empty] | 2034 | N | 6.751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2035 | N | 6.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2036 | N | 6.7199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2037 | N | 6.7045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2038 | N | 6.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2039 | N | 6.6736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2040 | N | 6.6583 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2041 | N | 6.643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2042 | N | 6.6277 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2043 | N | 6.6124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
[5 empty] | 2044 | N | 6.5972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
TOTAL: | 0 | 3000000 | 0 | 3000000 |  |  |  | 0 | 3000000 | 0 | 3000000 |  |  |  |  | 0 | 666666.6667 | 0 | 666666.6667 | 0 | 450000 | 0 | 450000 | 0 | 1116666.6667 | 0 | 1116666.6667 |  | 781666.6667 | 1451666.6667 |  | 6009457.4805 | 8584939.2579 | 11160421.0353

## SENSITIVITY
Include: | [5 empty] | Y |  |  |  |  | Y |  |  |  |  | Y |  |  |  |  | Y
Sensitivity
|  |  |  | Base (Do Nothing) |  |  |  |  | Option 1 (Myponga - SQWH) |  |  |  |  | Option 2 (Re-Insulation) |  |  |  |  | Option 3 (SHWF Islanded Ops)
Category | Scenario | Variance | Value | Cost | Gross Benefit | Net Benefit | Relative Benefit | Rank | Cost | Gross Benefit | Net Benefit | Relative Benefit | Rank | Cost | Gross Benefit | Net Benefit | Relative Benefit | Rank | Cost | Gross Benefit | Net Benefit | Relative Benefit | Rank
VCR ($/MWh) | Low | -30% | 20369.1233 | 6961973.7293 | 0 | -6961973.7293 | 0 | 4 | 4418310.6217 | 5051099.425 | 632788.8033 | 7594762.5325 | 2 | 1286738.4101 | 2107824.7704 | 821086.3604 | 7783060.0897 | 1 | 808793.2956 | 952516.2488 | 143722.9531 | 7105696.6824 | 3
| Med | 0% | 29098.7476 | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 4418310.6217 | 7215856.3214 | 2797545.6997 | 12743222.4558 | 1 | 1286738.4101 | 3011178.2435 | 1724439.8334 | 11670116.5895 | 2 | 808793.2956 | 1360737.4982 | 551944.2026 | 10497620.9587 | 3
| High | 30% | 37828.3719 | 12929379.7829 | 0 | -12929379.7829 | 0 | 4 | 4418310.6217 | 9380613.2178 | 4962302.5961 | 17891682.379 | 1 | 1286738.4101 | 3914531.7165 | 2627793.3065 | 15557173.0894 | 2 | 808793.2956 | 1768958.7477 | 960165.4521 | 13889545.235 | 3
Load Factor | Low | -30% | 70% | 6961973.7293 | 0 | -6961973.7293 | 0 | 4 | 4418310.6217 | 5051099.425 | 632788.8033 | 7594762.5325 | 2 | 1286738.4101 | 2107824.7704 | 821086.3604 | 7783060.0897 | 1 | 808793.2956 | 952516.2488 | 143722.9531 | 7105696.6824 | 3
| Med | 0% | 100% | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 4418310.6217 | 7215856.3214 | 2797545.6997 | 12743222.4558 | 1 | 1286738.4101 | 3011178.2435 | 1724439.8334 | 11670116.5895 | 2 | 808793.2956 | 1360737.4982 | 551944.2026 | 10497620.9587 | 3
| High | 30% | 130% | 12929379.7829 | 0 | -12929379.7829 | 0 | 4 | 4418310.6217 | 9380613.2178 | 4962302.5961 | 17891682.379 | 1 | 1286738.4101 | 3914531.7165 | 2627793.3065 | 15557173.0894 | 2 | 808793.2956 | 1768958.7477 | 960165.4521 | 13889545.235 | 3
Line Reliability (Outages/km/yr) | Low | -30% | 0.0105 | 6961973.7293 | 0 | -6961973.7293 | 0 | 4 | 4418310.6217 | 5051099.425 | 632788.8033 | 7594762.5325 | 2 | 1286738.4101 | 2107824.7704 | 821086.3604 | 7783060.0897 | 1 | 808793.2956 | 952516.2488 | 143722.9531 | 7105696.6824 | 3
| Med | 0% | 0.015 | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 4418310.6217 | 7215856.3214 | 2797545.6997 | 12743222.4558 | 1 | 1286738.4101 | 3011178.2435 | 1724439.8334 | 11670116.5895 | 2 | 808793.2956 | 1360737.4982 | 551944.2026 | 10497620.9587 | 3
| High | 30% | 0.0195 | 12929379.7829 | 0 | -12929379.7829 | 0 | 4 | 4418310.6217 | 9380613.2178 | 4962302.5961 | 17891682.379 | 1 | 1286738.4101 | 3914531.7165 | 2627793.3065 | 15557173.0894 | 2 | 808793.2956 | 1768958.7477 | 960165.4521 | 13889545.235 | 3
Discount Rate | Low | -25% | 2.63% | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 4807457.7048 | 7215856.3214 | 2408398.6166 | 12354075.3727 | 1 | 1392088.8617 | 3011178.2435 | 1619089.3818 | 11564766.1379 | 2 | 875012.4574 | 1360737.4982 | 485725.0408 | 10431401.7969 | 3
| Med | 0% | 3.507% | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 4418310.6217 | 7215856.3214 | 2797545.6997 | 12743222.4558 | 1 | 1286738.4101 | 3011178.2435 | 1724439.8334 | 11670116.5895 | 2 | 808793.2956 | 1360737.4982 | 551944.2026 | 10497620.9587 | 3
| High | 25% | 4.384% | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 4065454.426 | 7215856.3214 | 3150401.8954 | 13096078.6515 | 1 | 1190847.9054 | 3011178.2435 | 1820330.338 | 11766007.0942 | 2 | 748520.2855 | 1360737.4982 | 612217.2128 | 10557893.9689 | 3
Capital Costs | Low | -30% | 70% | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 3092817.4352 | 7215856.3214 | 4123038.8862 | 14068715.6423 | 1 | 900716.887 | 3011178.2435 | 2110461.3564 | 12056138.1126 | 2 | 566155.3069 | 1360737.4982 | 794582.1913 | 10740258.9474 | 3
| Med | 0% | 100% | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 4418310.6217 | 7215856.3214 | 2797545.6997 | 12743222.4558 | 1 | 1286738.4101 | 3011178.2435 | 1724439.8334 | 11670116.5895 | 2 | 808793.2956 | 1360737.4982 | 551944.2026 | 10497620.9587 | 3
| High | 30% | 130% | 9945676.7561 | 0 | -9945676.7561 | 0 | 4 | 5549193.589 | 7215856.3214 | 1666662.7323 | 11612339.4884 | 1 | 1672759.9331 | 3011178.2435 | 1338418.3104 | 11284095.0665 | 2 | 1051431.2843 | 1360737.4982 | 309306.2139 | 10254982.97 | 3

## CAPEXREG
Project Name | Myponga to Square Water Hole new 66kV line
Description | Construct new 66kV sub-transmission line between Square Water Hole and Myponga substations. Includes new 66kV line exit at both subtations and approx 19km of 66kV overhead line.
Total Cost ($M) | 20.9944
Constraint: | Loss of supply beyond Myponga or Square Water Hole for 66kV line fault. High load at risk.
YEAR | COST_% | COST_$M | LINE_$ | SUB_$
2023 | 19.05% | 4 | 3000000 | 1000000
2024 | 30.96% | 6.5 | 4875000 | 1625000
2025 | 49.99% | 10.494 | 7870500 | 2623500
TOTAL |  | 20.994 | 15745500 | 5248500
EQUIP | QTY | COST_$M | %
L66kV508 | 19 | 16.9476 | 80.72%
CB66kVBay | 2 | 1.3648 | 6.501%
Prot66kVLine | 2 | 0.47697 | 2.272%
Bus66kVSection | 2 | 0.63669 | 3.033%
InfraExtensive | 1 | 1.2891 | 6.14%
SCADAMedium | 2 | 0.27929 | 1.33%
TOTAL |  | 20.9944 | 100%
%
LINE | 75%
SUB | 25%
TOTAL | 100%
Line Re-Insulation Costing
Decision Reports Oct 2018
| COST_% | COST_$M
Willunga - SQWH | 24.08% | 1289000
SQWH - Victor Harbor | 25.44% | 1361951
Willunga - Myponga | 24.41% | 1307036
Myponga - Yankalilla | 26.07% | 1395985
SUBTOTAL: | 48.49% | 2596036
TOTAL: | 100% | 5353972