## OMQ LOS events
Outage Month Query
[14 empty] | X= | 0.05 | 0.4
WASP Outage Key | PROMS Request No | Month | Start Time | End Time | Duration (Min) | Element ID | Element Name | Element Type | Request Type | Request Reason | Request Instigator | Out of Service | Unserved MW Min | System Minutes | LOS > X | LOS > Y | Comments | CAPEX | AER STPIS | LOS Duration
24243 | 1669 | Jul 2011 | 2011-07-08 03:42 | 2011-07-08 04:07 | 25 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Unknown | Transend | Yes | 3457 | 1.8447 | 1 | 1 | IR1131 CS-KI-KR tripped with loss of supply at Kingston, Knights Road, Kermandie and Huon River substations. 3 separate LOS durations are summed | No | Non-Critical | 34
24244 | 8903 | Jul 2011 | 2011-07-12 11:35 | 2011-07-12 11:39 | 4 | E0728 | NH 11 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Yes | 33 | 0.0176 | FALSE | FALSE | IR1140 North Hobart feeders tripped during planned work IR1140 North Hobart feeders tripped during planned work | No | Undefined | 4
24403 | 1677 | Jul 2011 | 2011-07-14 16:05 | 2011-07-15 22:52 | 1847 | E0374 | KI 110/11 kV T2 Transformer Circuit | Transformer | Fault | Ancillary Equipment Failure | Transend | Yes | 2281 | 1.2172 | 1 | 1 | IR1134 KI T2 tripped on Bucholz alarm and caused loss of supply at Kingston substation. | No | Non-Critical | 89
24883 | 1687 | Sep 2011 | 2011-09-14 14:13 | 2011-09-14 15:13 | 60 | E0784 | PL 22 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Yes | 533 | 0.2844 | 1 | FALSE | IR1161 Port Latta 22kV B Bus tripped due to error during planned work. | No | Undefined | 56
24927 | 1689 | Sep 2011 | 2011-09-19 06:49 | 2011-09-19 10:17 | 208 | E0722 | NT 110 kV XBus | Bus | Fault | Abnormal Operating Conditions | Transend | Yes | 3940 | 2.1025 | 1 | 1 | IR1165 Newton 110 kV bus bar tripped due to T2 Bucholz trip caused b y low oil level, causing loss of supply. | No | Undefined | 208
24782 | 1688 | Sep 2011 | 2011-09-19 09:06 | 2011-09-19 09:31 | 25 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Yes | 1021 | 0.5448 | 1 | 1 | IR1164 Farrell-Rosebery-Queenstown transmission circuit tripped due to equipment failure (A helical dead end failed on FA-RB). | No | Non-Critical | 146
24926 | 1690 | Sep 2011 | 2011-09-19 19:43 | 2011-09-19 19:43 | 0 | E0402 | BU-ST 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 209 | 0.1115 | 1 | FALSE | IR1166 BU-PL, BU-ST, SB-WN-ST and PL-ST 110 kV transmission circuits tripped with lightning in area. Loss of supply at Port Latta Substation. | No | Non-Critical | 17
25082 | 1699 | Oct 2011 | 2011-10-26 22:34 | 2011-10-27 00:53 | 139 | E1068 | GT-GC 220 kV Transmission Circuit | Transmission | Fault | Basslink | Basslink | Yes | 48480 | 25.8698 | 1 | 1 | IR1179 GT-GC transmission circuit tripped, suspect filter protection trip at Basslink converter station. | No | Undefined | 139
25258 | 1712 | Nov 2011 | 2011-11-24 09:29 | 2011-11-24 09:58 | 29 | E1702 | TE 110 kV Bus SPS | Bus | Fault | Pending Investigation | Basslink | Yes | 818 | 0.4365 | 1 | 1 | SPS trip Temco load | No | Undefined
25238 | 1714 | Nov 2011 | 2011-11-26 09:00 | 2011-11-26 14:54 | 354 | E0617 | GO 220/22 kV T6 Transformer Circuit | Transformer | Fault | Generator | Generator Request | Yes | 110 | 0.0587 | 1 | FALSE | IR?? Gordon Substation 200/22 kV T1 and 220 kV B Bus bar trip | No | Non-Critical | 6366
25354 | 1795 | Dec 2011 | 2011-12-19 10:22 | 2011-12-20 21:11 | 2089 | E0193 | SO 110/22 kV T2 Transformer Circuit | Transformer | Fault | Moisture Ingress | Transend | Yes | 312 | 0.1665 | 1 | FALSE | IR1211 Sorell Substation 110/22kV transformer T2 tripped due to water ingress. Restoration date and time to be determined | No | Non-Critical | 84
25519 | 1803 | Feb 2012 | 2012-02-01 00:31 | 2012-02-01 00:44 | 13 | E0237 | RI 11 kV Q3 Feeder Circuit | Feeder | Fault | Ancillary Equipment Failure | MI | Yes | 272 | 0.1451 | 1 | FALSE | IR1226 Nyrstar feeders tripped, suspect due to operation of harmonic filter. | No | Undefined | 13
25661 | 1809 | Feb 2012 | 2012-02-14 07:34 | 2012-02-14 07:55 | 21 | E0323 | BY 6.6 kV E Bus | Bus | Fault | Human Error During Planned Work | Transend | Yes | 20 | 0.0107 | FALSE | FALSE | IR1132 Boyer 6.6 kV E Bus Bar tripped during planned work. | No | Undefined | 21
25663 | 1812 | Feb 2012 | 2012-02-25 21:08 | 2012-02-25 21:13 | 5 | E0940 | UL 22 kV A Bus | Bus | Fault | Poor Construction | Transend | Yes | 153 | 0.0816 | 1 | FALSE | IR1134 Ulverstone feeders (all) tripped during bush fire response, suspect script calc error. | No | Undefined | 41
26161 | 1813 | Mar 2012 | 2012-03-15 23:18 | 2012-03-15 23:25 | 7 | E0276 | PM-AL 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 45 | 0.024 | FALSE | FALSE | IR1276 Palmerston-Arthurs Lake 110kV transmission circuit tripped with lightning in the area, suspect lightning. | No | Non-Critical | 7
26162 | 1814 | Mar 2012 | 2012-03-20 14:33 | 2012-03-20 14:46 | 13 | E0373 | KI 110/11 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Yes | 136 | 0.0726 | 1 | FALSE | IR1273 Kingston T2 tripped due to an error during commissioning. | No | Non-Critical | 13
26186 | 1816 | Apr 2012 | 2012-04-06 19:35 | 2012-04-06 21:14 | 99 | E0397 | BU 220/110 kV T2 Transformer Circuit | Transformer | Fault | Adverse Weather | Transend | Yes | 1174 | 0.6265 | 1 | 1 | IR1135 Burnie 110 kV transmission line circuits tripped during severe lightning with LOS at Burnie, Ulverstone, Emu Bay, Port Latta, Smithton and Hampshire substations. | No | Non-Critical | 30
26244 | 1822 | Apr 2012 | 2012-04-11 12:46 | 2012-04-11 12:56 | 10 | E0030 | CS-KI-KR 110 kV Transmission Circuit (changed to E1955) | Transmission | Fault | Human Error During Planned Work | Transend | Yes | 145 | 0.0774 | 1 | FALSE | IR1275 CS-KI-KR 110 kV transmission line circuit tripped during planned work when a tree contacted line. | No | Non-Critical | 11
26501 | 1830 | May 2012 | 2012-05-07 23:47 | 2012-05-08 02:06 | 139 | E0316 | BY 6.6 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 1586 | 0.8463 | 1 | 1 | IR1282 Boyer 6.6kV A and B bus circuits tripped due to a protection deficiency following faulted customer feeder. | No | Undefined | 139
26558 | 1831 | May 2012 | 2012-05-10 10:36 | 2012-05-10 11:53 | 77 | E0293 | AL 110/6.6 kV T1 Transformer Circuit | Transformer | Fault | Unknown | Transend | Yes | 493 | 0.2631 | 1 | FALSE | IR1140 Arthurs Lake T1 transformer circuit tripped with loss of supply at Arthurs Lake when Hydro Pumps were started. investigation not conclusive due to lack of SOE data and lack of protection testing/ investigation. | No | Non-Critical | 77
26502 | 1832 | May 2012 | 2012-05-11 23:02 | 2012-05-12 00:11 | 69 | E0316 | BY 6.6 kV A Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 771 | 0.4114 | 1 | 1 | IR1284 Boyer 6.6 kV A and B bus circuits tripped due to protection deficiency following faulted customer feeder. | No | Undefined | 65
26557 | 1834 | May 2012 | 2012-05-12 05:46 | 2012-05-12 06:00 | 14 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 41 | 0.0219 | FALSE | FALSE | IR1142 FA-RB-QT and QT-NT 110kV transmission circuit tripped with lightning in area with loss of supply to Aurora (Henty Gold) | No | Non-Critical | 12
27177 | 1118480 | Jul 2012 | 2012-07-11 23:29 | 2012-07-12 06:46 | 437 | E1616 | HR 11 kV A Bus Circuit | Bus | Fault | Switching Error | Transend | Yes | 105 | 0.056 | 1 | FALSE | IR1217 Huon River customer lost supply for a planned outage with no notification. | No | Undefined | 438
27345 | 1848 | Aug 2012 | 2012-08-04 08:00 | 2012-08-04 11:40 | 220 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Wildlife | Transend | Yes | 29 | 0.0155 | FALSE | FALSE | IR1159 DB T1 transformer circuit tripped with LOS at Derwent Bridge | No | Non-Critical | 220
27349 | 1858 | Sep 2012 | 2012-09-04 13:44 | 2012-09-04 13:48 | 4 | E0115 | CS 11 kV Q2 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Yes | 10 | 0.0053 | FALSE | FALSE | IR1169 Chapel Street feeders (2) tripped during protection testing. | No | Undefined | 4
27620 | 1856 | Sep 2012 | 2012-09-07 18:23 | 2012-09-07 18:39 | 16 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Fatigue | Transend | Yes | 114 | 0.0608 | 1 | FALSE | IR1167 Queenstown-Newton 110 kV transmission circuit tripped with loss of supply at Newton Substation. | No | Non-Critical | 16
27417 | 1857 | Sep 2012 | 2012-09-09 15:38 | 2012-09-09 19:16 | 218 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Insulation Failure | Transend | Yes | 540 | 0.2882 | 1 | FALSE | IR1168 LF-SO-TB 110kV transmission circuit was forced out due to insulator damage by shooting. | No | Non-Critical | 221
27619 | 1859 | Sep 2012 | 2012-09-13 11:31 | 2012-09-13 13:17 | 106 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Poor Construction | Transend | Yes | 4353 | 2.3228 | 1 | 1 | IR1113 Farrell-Rosebery-Queenstown 110kV transmission circuit tripped with loss of supply to West Coast. | No | Non-Critical | 121
27904 | 1862 | Oct 2012 | 2012-10-11 09:24 | 2012-10-11 09:28 | 4 | E0274 | PM-AV 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Yes | 62 | 0.0331 | FALSE | FALSE | IR1171 PM-AV 110 kV transmission line circuit tripped due to incorrect VT selection during planned work. LOS at Avoca and St Marys. | No | Non-Critical | 6
27973 | 1867 | Nov 2012 | 2012-11-09 12:01 | 2012-11-09 12:07 | 6 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 13 | 0.0069 | FALSE | FALSE | IR1176 LF-SO-TB 110 kV transmission circuit tripped with lightning in area. | No | Non-Critical | 5
27974 | 1868 | Nov 2012 | 2012-11-12 11:05 | 2012-11-12 11:14 | 9 | E0538 | SH-FA 1 220 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 1405 | 0.7497 | 1 | 1 | IR1177 SH-FA 1 and 2 220 kV transmission circuits tripped due to lightning strike with loss of supply to West Coast. | No | Critical | 40
28118 | 1870 | Nov 2012 | 2012-11-14 12:46 | 2012-11-14 13:11 | 25 | E0857 | RB 110/44 kV T2 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 599 | 0.3196 | 1 | FALSE | IR1179 Rosebery T2 tripped possibly due to grading error with new T2 protection. | No | Non-Critical | 32
28120 | 1871 | Nov 2012 | 2012-11-27 07:32 | 2012-11-27 07:47 | 15 | E0504 | GT 220 kV B Bus | Bus | Fault | Human Error During Planned Work | Transend | Yes | 1901 | 1.0144 | 1 | 1 | IR1180 George Town 220 kV Bus Bar tripped due to testing error | No | Undefined | 18
28121 | 1875 | Nov 2012 | 2012-11-30 20:37 | 2012-11-30 20:59 | 22 | E0470 | KR 110/11 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 173 | 0.0923 | 1 | FALSE | IR1187 Knights Road transformer circuits tripped with loss of supply. | No | Non-Critical | 21
28122 | 1876 | Nov 2012 | 2012-11-30 21:17 | 2012-12-01 | 163 | E0276 | PM-AL 110 kV Transmission Circuit | Transmission | Fault | Fire (Bush) | Force Majeure | Yes | 45092 | 24.0619 | 1 | 1 | IR1188 PM-AL 110 kV transmission circuit tripped due to bushfire, with loss of supply at Arthurs Lake. | No | Non-Critical | 6964
28171 | 1882 | Dec 2012 | 2012-12-04 14:12 | 2012-12-04 14:27 | 15 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 301 | 0.1606 | 1 | FALSE | IR1194 Farrell-Rosebery-Queenstown 110 kV transmission circuit tripped - Suspected Lightning | No | Non-Critical | 22
28176 | 1887 | Dec 2012 | 2012-12-13 06:06 | 2012-12-13 06:12 | 6 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 145 | 0.0774 | 1 | FALSE | IR1199 FA-RB-QT 110 kV transmission circuit tripped with Lightning in area. | No | Non-Critical | 12
28296 | 1888 | Dec 2012 | 2012-12-15 11:05 | 2012-12-17 18:08 | 3303 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Fault | Internal Fault | Transend | Yes | 142 | 0.0758 | 1 | FALSE | IR1200 Que T1 transformer tripped | No | Non-Critical | 1267
28297 | 1889 | Dec 2012 | 2012-12-24 14:18 | 2012-12-24 14:38 | 20 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 70 | 0.0374 | FALSE | FALSE | IR1201 LF-SO-TB 110 kV transmission circuit tripped with lightning in area | No | Non-Critical | 24
28635 | 1892 | Feb 2013 | 2013-02-06 06:26 | 2013-02-06 07:29 | 63 | E1878 | SL 110/22 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 299 | 0.1596 | 1 | FALSE | IR1215 St Leonards T1 and T2 transformer circuits tripped folllowing a feeder fault due to a protection grading issue.. | No | Non-Critical | 63
28833 | 1895 | Mar 2013 | 2013-03-05 07:25 | 2013-03-05 07:37 | 12 | E0779 | PL 22 kV B2 Feeder Circuit | Feeder | Fault | Intertrip | MI | Yes | 95 | 0.0507 | 1 | FALSE | IR1230 Port Latta feeders tripped, suspect Grange Resources misoperation in their yard. | No | Undefined
28834 | 1898 | Mar 2013 | 2013-03-10 14:15 | 2013-03-10 14:23 | 8 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 165 | 0.088 | 1 | FALSE | IR1233 FA-QU-SR-HM 110 kV line tripped due to lightning. | No | Non-Critical | 8
28978 | 1913 | Mar 2013 | 2013-03-27 09:03 | 2013-03-27 09:16 | 13 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Yes | 34 | 0.0181 | FALSE | FALSE | IR1260 QT-NT 110 kV transmission circuit tripped during work for new Newton T2 circuit. | No | Non-Critical | 13
29191 | 1915 | Apr 2013 | 2013-04-09 12:19 | 2013-04-09 12:32 | 13 | E0233 | RI 11 kV D3 Feeder Circuit | Feeder | Fault | Intertrip | MI | Yes | 180 | 0.0961 | 1 | FALSE | IR1262 Risdon D352A 11 kV feeder tripped due to intertrip from Nyrstar. | No | Undefined | 13
29420 | 1918 | Apr 2013 | 2013-04-27 13:58 | 2013-04-28 12:22 | 1344 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Yes | 538 | 0.2871 | 1 | FALSE | IR1300 LF-SO-TB 110 kV transmission line circuit tripped due to broken conductor at a time of severe winds | No | Non-Critical | 503
29421 | 1919 | May 2013 | 2013-05-01 03:47 | 2013-05-01 06:40 | 173 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Yes | 18 | 0.0096 | FALSE | FALSE | IR1301 Derwent Bridge 110/22 kV T1 transformer circuit tripped following a feeder fault due to a protection grading issue. | No | Non-Critical | 173
29422 | 1920 | May 2013 | 2013-05-09 16:33 | 2013-05-09 17:10 | 37 | E0792 | QT 110 kV Bus | Bus | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 464 | 0.2476 | 1 | FALSE | IR1302 Queenstown 110 kV A Bus tripped due to incorrect protection settings at QT after an inter-trip caused by incorrect isolation for planned work at Newton. | No | Undefined | 48
29424 | 1922 | May 2013 | 2013-05-22 11:16 | 2013-05-22 11:33 | 17 | E0234 | RI 11 kV E3 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Yes | 262 | 0.1398 | 1 | FALSE | IR1304 Risdon E352 feeder tripped due to error during planned work on SCADA. The consequent overload of customer plant caused a loss of supply. | No | Undefined | 18
29626 | 1929 | Jun 2013 | 2013-06-12 14:54 | 2013-06-13 12:38 | 1304 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Insulation Failure | Transend | Yes | 26638 | 14.2145 | 1 | 1 | IR1334 FA-QU-SR-HM 110 kV transmission circuit tripped due to failed insulator. | No | Non-Critical | 1298
29643 | 1930 | Jun 2013 | 2013-06-13 11:00 | 2013-06-13 11:09 | 9 | E0293 | AL 110/6.6 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | No | 1 | 0.0005 | FALSE | FALSE | IR1335 Arthurs Lake T1 tripped during testing of Hydro pump circuit. T1 was out of service at the time on PROMS 123203. marked in service due to cct being oos at the time | No | Non-Critical
29848 | 1935 | Jul 2013 | 2013-07-16 12:50 | 2013-07-16 15:36 | 166 | E0293 | AL 110/6.6 kV T1 Transformer Circuit | Transformer | Fault | Intertrip | Generator Request | No | 1 | 0.0005 | FALSE | FALSE | IR1341 Arthurs Lake T1 transformer tripped due to intertrip from Hydro at pump start. marked in service as T1 oos at the time. fault oput against feeder as T1 out of service at the time | No | Non-Critical | 169
29849 | 1938 | Jul 2013 | 2013-07-16 19:11 | 2013-07-17 14:29 | 1158 | E1782 | MT 33 kV A Bus | Bus | Fault | Insulation Failure | Transend | Yes | 535 | 0.2855 | 1 | FALSE | IR1342 Mornington 33kV D252 tripped due to equipment failure, with smoke causing forced outage of 33 kV A and B buses. 33kV B Bus energised at 1941. Howrah Zone energised at 1952. Cambridge Zone backfed by Aurora at 1958. Fire Brigade have left site. | No | Not in WASP | 47
30274 | 1942 | Aug 2013 | 2013-08-05 19:51 | 2013-08-05 20:07 | 16 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Yes | 2 | 0.0011 | FALSE | FALSE | IR22 Derwent Bridge T1 transformer circuit tripped due to a protection grading issue following a feeder fault. | No | Non-Critical | 15
30277 | 1946 | Aug 2013 | 2013-08-19 01:36 | 2013-08-19 03:20 | 104 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 527 | 0.2812 | 1 | FALSE | IR26 QT-NT 110 kV transmission circuit tripped with lightning in area. | No | Non-Critical | 176
30314 | 1949 | Aug 2013 | 2013-08-20 06:49 | 2013-08-20 06:53 | 4 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Yes | 1 | 0.0005 | FALSE | FALSE | IR30 DB T1 transformer circuit tripped following a feeder fault due to SEF protection being out of service. | No | Non-Critical | 3
30467 | 1956 | Sep 2013 | 2013-09-24 16:33 | 2013-09-24 16:57 | 24 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Yes | 925 | 0.4936 | 1 | 1 | IR1430 RB T1 and FA-RB-QT 110 kV circuits tripped following a human error during planned maintenance work, with loss of supply at Rosebery, Queenstown and Newton. | No | Non-Critical | 60
30602 | 1961 | Oct 2013 | 2013-10-01 00:25 | 2013-10-01 00:36 | 11 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 1051 | 0.5608 | 1 | 1 | IR1449 FA-JB 220 kV and FA-RB-QT 110 kV transmission circuits tripped with LOS at Queenstown and Newton, suspect lightning. | No | Non-Critical | 220
30604 | 1960 | Oct 2013 | 2013-10-01 03:47 | 2013-10-01 03:54 | 7 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 126 | 0.0672 | 1 | FALSE | IR1451 FA-RB-QT 110 kV transmission circuit tripped due to lightning with LOS at Queenstown. | No | Non-Critical | 14
30653 | 1966 | Oct 2013 | 2013-10-15 15:18 | 2013-10-15 15:24 | 6 | E0098 | CS 11 kV B Bus | Bus | Fault | Internal Fault | Transend | Yes | 23 | 0.0123 | FALSE | FALSE | IR1484 Chapel St 11 kV B Bus tripped during planned work due to an incorrect CB status indication caused by an internal wiring failure. | No | Undefined | 6
30896 | 1986 | Dec 2013 | 2013-12-11 00:42 | 2013-12-11 01:52 | 70 | E0318 | BY 6.6 kV B Bus | Bus | Fault | Protection & Control Device | Transend | Yes | 855 | 0.4562 | 1 | 1 | IR1532 Boyer 6.6 kV B Bus tripped due to a protection mal-operation following a feedr fault. | No | Undefined | 71
31170 | 1992 | Jan 2014 | 2014-01-20 12:17 | 2014-01-20 12:24 | 7 | E0154 | MB 110/22 kV T4 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Yes | 11 | 0.0059 | FALSE | FALSE | IR1556 Meadowbank T4 transformer circuit tripped due to incorrect isolation during planned work. | No | Non-Critical | 7
31232 | 1996 | Feb 2014 | 2014-02-09 14:12 | 2014-02-09 14:22 | 10 | E0191 | LF-SO-TB 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 30 | 0.016 | FALSE | FALSE | IR1571 LF-SO-TB 110 kV transmission circuit tripped with lightning in area. | No | Non-Critical | 10
31347 | 2003 | Feb 2014 | 2014-02-15 19:56 | 2014-02-15 19:56 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 18 | 0.0096 | FALSE | FALSE | IR1587 FA-RB-QT tripped and autoreclosed with lightning in area, and as a consequence feeders at Newton and Queenstown tripped with loss of supply at Queenstown. | No | Non-Critical | 5
31350 | 2008 | Feb 2014 | 2014-02-27 07:33 | 2014-02-27 10:14 | 161 | E0276 | PM-AL 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Yes | 1025 | 0.547 | 1 | 1 | IR1596 Trasnsient fault on TU-LE-WA 1 caused PM-AL and TU-LE-WA 1 transmission circuits to trip. Due to protection mal-operation following there was a loss of supply at Arthurs Lake. LOS at Arthurs Lake due to protection settings issue | No | Non-Critical | 161
31707 | 444444444 | Mar 2014 | 2014-03-05 07:43 | 2014-03-05 08:07 | 24 | E0317 | BY 6.6 kV A3 Feeder Circuit | Feeder | Fault | Switching Error | Transend | Yes | 55 | 0.0293 | FALSE | FALSE | IR1597 Boyer 6.6 kV A352 feeder circuit was opened when on load due to a switching error. | No | Undefined | 23
32065 | 2016 | Jun 2014 | 2014-06-26 04:10 | 2014-06-26 04:28 | 18 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 280 | 0.1494 | 1 | FALSE | IR1634 FA-RB-QT 110 kV and FA-JB 220 kV transmission circuits tripped with lightning in the vicinity with loss of supply at Queenstown and Newton. | No | Non-Critical | 28
32093 | 2020 | Jul 2014 | 2014-07-22 10:07 | 2014-07-23 15:14 | 1747 | E1941 | NT 110/11 kV T2 Transformer Circuit | Transformer | Fault | Protection & Control Device | Transend | Yes | 1179 | 0.6291 | 1 | 1 | IR1637 Newton T2 transformer circuit tripped due to a faulty tap changer with loss of supply to Newton Pumps. | No | Non-Critical | 1744
32235 | 2023 | Jul 2014 | 2014-07-29 20:26 | 2014-07-29 20:26 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 22 | 0.0117 | FALSE | FALSE | IR1640 FA-RB-QT 110 kV transmission circuit tripped and automatically reclosed affecting CMT and Lake Margaret generation. | No | Non-Critical | 13
32236 | 2024 | Jul 2014 | 2014-07-29 22:45 | 2014-07-30 01:16 | 151 | E1614 | KR-HR-KE 110 kV Transmission Circuit | Transmission | Fault | Vegetation | Transend | Yes | 602 | 0.3212 | 1 | FALSE | IR1641 KR-HR-KE 110 kV transmission circuit tripped due to a broken conductor on the HR tee section. note that HuonRiver is not included in system minutes calc as the non prescribed Tee sectionto HR caused the fault. | No | Non-Critical | 153
32239 | 2026 | Jul 2014 | 2014-07-31 12:16 | 2014-07-31 13:05 | 49 | E0484 | GT 110/22 kV T5 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Yes | 115 | 0.0614 | 1 | FALSE | IR1643 George Town circuits tripped during planned protection work. GT-TV 2 out of service on PROMS at time of trip | No | Non-Critical | 49
32767 | 2032 | Oct 2014 | 2014-10-24 11:12 | 2014-10-24 13:22 | 130 | E1027 | QU 22 kV A Bus | Bus | Fault | Customer | MI | Yes | 16 | 0.0085 | FALSE | FALSE | IR1655 Que 22 kV bus bar tripped following a customer feeder fault | No | Undefined | 70
32768 | 2033 | Oct 2014 | 2014-10-27 02:38 | 2014-10-27 02:38 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 34 | 0.0181 | FALSE | FALSE | IR1656 FA-RB-QT 110 kV transmission circuit tripped and reclosed with lightning in the vicinity with loss of supply at Queenstown due under frequency protection operation. | No | Non-Critical | 15
33644 | 2064 | Apr 2015 | 2015-04-26 08:30 | 2015-04-26 08:36 | 6 | E0153 | MB 110 kV Bus | Bus | Fault | Generator | Transend | Yes | 17 | 0.0091 | FALSE | FALSE | IR1688 Meadowbank busbar tripped due to incorrect protection isolation during testing. | No | Undefined | 6
33674 | 2065 | May 2015 | 2015-05-05 10:04 | 2015-05-05 10:21 | 17 | E0298 | AV-SM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 1525 | 0.8138 | 1 | 1 | IR? AV-SM 110 transmission circuit tripped during severe weather due to windborne bark. | No | Non-Critical | 233
33708 | 2071 | May 2015 | 2015-05-12 11:48 | 2015-05-12 11:48 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 577 | 0.3079 | 1 | FALSE | IR1695 FA-RB-QT 110 kV transmission circuit tripped with loss of supply at Queenstown and Newton substations. | No | Non-Critical | 44
33805 | 2073 | May 2015 | 2015-05-29 16:10 | 2015-05-29 16:16 | 6 | E0510 | GT-CO 4 220 kV Transmission Circuit | Transmission | Fault | Human Error During Planned Work | Transend | Yes | 656 | 0.3501 | 1 | FALSE | IR1697 GT-CO 4 220 kV transmission circuit tripped due to switching error during planned work. | No | Non-Critical | 6
33931 | 2075 | Jun 2015 | 2015-06-01 08:21 | 2015-06-01 08:30 | 9 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 185 | 0.0987 | 1 | FALSE | IR1699 FA-QU-SR-HM 110 kV transmission circuit tripped due to ice loading. | No | Non-Critical | 17
34028 | 2078 | Jul 2015 | 2015-07-03 08:01 | 2015-07-03 08:03 | 2 | E0678 | TR 110 kV D Bus | Bus | Fault | Human Error During Planned Work | Transend | Yes | 34 | 0.0181 | FALSE | FALSE | IR2078 Trevallyn 22 kV D Bus was being fed by a Mowbray super feeder when the feeder tripped on directional over current causing loss of supply. | No | Undefined | 2
34222 | 2086 | Sep 2015 | 2015-09-24 11:54 | 2015-09-24 12:45 | 51 | E1653 | EL 110/11 kV T2 Transformer Circuit | Transformer | Fault | Human Error During Planned Work | Transend | Yes | 3 | 0.0016 | FALSE | FALSE | IIR 1711 Electrona T2 was tripped while removing a bird nest from conservator tank | No | Non-Critical | 3
34224 | 2087 | Sep 2015 | 2015-09-28 21:36 | 2015-09-28 21:47 | 11 | E1065 | QU 22 kV A2 Feeder Circuit | Feeder | Fault | Adverse Weather | Transend | Yes | 1 | 0.0005 | FALSE | FALSE | IR1272 Que Substation incomer breaker A552 tripped during inclement weather. | No | Undefined | 11
34342 | 2089 | Oct 2015 | 2015-10-20 11:06 | 2015-10-20 13:27 | 141 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Yes | 13 | 0.0069 | FALSE | FALSE | IR2089 BU-HM 110 kV transmission circuit tripped due to unknown cause. | No | Non-Critical | 87
34396 | 2092 | Nov 2015 | 2015-11-11 06:39 | 2015-11-11 12:12 | 333 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Unknown | Transend | Yes | 12 | 0.0064 | FALSE | FALSE | IR2092 BU-HM 110 kV transmission circuit tripped due to unknown cause, with loss of supply to Surrey Hills Chip Mill. | No | Non-Critical | 53
34397 | 2093 | Nov 2015 | 2015-11-13 13:49 | 2015-11-13 13:52 | 3 | E0101 | CS 11 kV C Bus | Bus | Fault | Human Error During Planned Work | Transend | Yes | 7 | 0.0037 | FALSE | FALSE | IR2093 Chapel Street 11kV C Bus tripped during planned testing work, with loss of supply to DNSP. | No | Undefined | 3
34398 | 2094 | Nov 2015 | 2015-11-25 15:02 | 2015-11-26 13:03 | 1321 | E0169 | TU-BG-DB 110 kV Transmission Circuit | Transmission | Fault | Vegetation | Transend | Yes | 82 | 0.0438 | FALSE | FALSE | IR2094 TU-DB-BG 110 kV transmission circuit tripped due to tree on line with loss of supply at Derwent Bridge. | No | Non-Critical | 418
34603 | 2106 | Jan 2016 | 2016-01-28 09:49 | 2016-01-28 09:56 | 7 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 1 | 0.0005 | FALSE | FALSE | IR2106 BU-HM 110 kV transmission circuit tripped with lightning in area. | No | Non-Critical | 7
35057 | 2125 | Apr 2016 | 2016-04-25 16:51 | 2016-04-25 16:57 | 6 | E0407 | DB 110/22 kV T1 Transformer Circuit | Transformer | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 1 | 0.0005 | FALSE | FALSE | IR2125 Derwent Bridge 110/22 kV T1 transformer circuit tripped due to incorrect protection settings. | No | Non-Critical | 6
35258 | 2127 | May 2016 | 2016-05-01 02:39 | 2016-05-01 02:39 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 99 | 0.0528 | 1 | FALSE | IR2127 FA-RB 110 kV transmission circuit tripped and reclosed twice, with loss of supply at Newton (pumps), Queenstown MI and operation of Lake Margaret anti islanding scheme. | No | Non-Critical | 35
35259 | 2129 | May 2016 | 2016-05-01 04:07 | 2016-05-01 04:07 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 13 | 0.0069 | FALSE | FALSE | IR2129 FA-RB 110 kV and FA-JB 220 kV transmission circuits tripped, with loss of supply at Newton (pumps) and Queenstown MI, with lightning in area. | No | Non-Critical | 4
35263 | 2134 | May 2016 | 2016-05-13 01:07 | 2016-05-13 15:18 | 851 | E0400 | BU-HM 110 kV Transmission Circuit | Transmission | Fault | Mechanical Failure | Transend | Yes | 2 | 0.0011 | FALSE | FALSE | IR2134 BU-HM 110 kV transmission circuit tripped due to equipment failure and locked out. | No | Non-Critical | 8
35265 | 2135 | May 2016 | 2016-05-17 10:13 | 2016-05-17 10:21 | 8 | E1702 | TE 110 kV Bus SPS | Bus | Fault | Human Error During Planned Work | MI | Yes | 146 | 0.0779 | 1 | FALSE | IR2135 TEMCO SPS Load Block 1 tripped due to incorrect secondary isolation during planned work. Load shedding occurred due to incorrect inhibit signal configuration within TEMCO RTU. | No | Undefined | 8
35350 | 2142 | Jul 2016 | 2016-07-12 20:26 | 2016-07-12 20:26 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 22 | 0.0117 | FALSE | FALSE | IR2142 FA-RB-QT 110 kV transmission circuit tripped and reclosed with lightning in area and with loss of supply to CMT at Queenstown. | No | Non-Critical | 12
35477 | 2148 | Aug 2016 | 2016-08-12 20:48 | 2016-08-12 20:48 | 0 | E0406 | FA-QU-SR-HM 110 kV Transmission Circuit | Transmission | Fault | Protection Design / Calculations Incorrect | Transend | Yes | 66 | 0.0352 | FALSE | FALSE | IR2148 FA-QU-SR-HM 110 kV transmission circuit tripped and auto reclosed, with LOS at Que and savage River. | No | Non-Critical | 16
35478 | 2149 | Aug 2016 | 2016-08-13 19:01 | 2016-08-13 19:01 | 0 | E0721 | QT-NT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Pumping Load | Yes | 6 | 0.0032 | FALSE | FALSE | IR2149 QT-NT 110 kV transmission circuit tripped and automatically reclosed with lightning in area, with LOS to Newton Pumps. | No | Non-Critical | 2
35587 | 2151 | Sep 2016 | 2016-09-29 11:44 | 2016-09-29 11:47 | 3 | E1782 | MT 33 kV A Bus | Bus | Fault | Human Error During Planned Work | Transend | Yes | 30 | 0.016 | FALSE | FALSE | IR2151 Mornington 33 kV Bus tripped during planned work for protection testing. | No | Not in WASP | 3
35762 | 2155 | Nov 2016 | 2016-11-21 09:22 | 2016-11-21 09:22 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 12 | 0.0064 | FALSE | FALSE | IR2155 FA-RB-QT 110 kV transmission circuit tripped and auto reclosed with lightning in area. | No | Non-Critical | 20
35906 | 2163 | Dec 2016 | 2016-12-20 09:39 | 2016-12-20 09:59 | 20 | E0409 | SH-CE 220 kV Transmission Circuit | Transmission | Fault | System Condition | Transend | Yes | 3102 | 1.6553 | 1 | 1 | IR2163 SH-CE, SH-WI,SH-LE,SH-FI 220 kV and SH-DG 110 kV transmission circuit tripped due to backup NCSPS action following attempted restoration of SH-GT 2. UFLS action then followed, with 163 MW load shedding to Nyrstar and BBA MIs. | No | Non-Critical | 50
35909 | 2166 | Dec 2016 | 2016-12-29 19:57 | 2016-12-29 19:57 | 0 | E0720 | FA-RB-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 10 | 0.0053 | FALSE | FALSE | IR2166 FA-RB-QT 110 kV transmission circuit tripped and auto reclosed. Newton D352 circuit breaker also tripped at the same time. Lake Margaret anti-islanding scheme operated at the same time. | No | Non-Critical | 5
36238 | 2172 | Mar 2017 | 2017-03-09 06:33 | 2017-03-09 08:48 | 135 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Fault | Protection & Control Device | Transend | Yes | 6 | 0.0032 | FALSE | FALSE | IR2172 Que T1 110/22 kV transformer tripped due to protection relay mal-operation. | No | Non-Critical | 135
36313 | 2179 | Apr 2017 | 2017-04-03 06:46 | 2017-04-03 06:58 | 12 | E0322 | BY 6.6 kV D3 Feeder Circuit | Feeder | Fault | Human Error During Planned Work | Transend | Yes | 171 | 0.0912 | 1 | FALSE | IR2179 Boyer D352 circuit breaker tripped due to operational error causing los of supply. | No | Undefined | 12
36450 | 2186 | May 2017 | 2017-05-26 10:05 | 2017-05-26 10:39 | 34 | E1029 | SR 22 kV G2 Feeder Circuit | Feeder | Fault |  | MI | Yes | 329 | 0.1756 | 1 | FALSE | IR2186 Savage River 22 kV G feeder tripped due to................................... | No | Undefined | 34
36619 | 2190 | Jun 2017 | 2017-06-09 10:40 | 2017-06-09 11:01 | 21 | E0951 | WA 110/22 kV T1 Transformer Circuit | Transformer | Fault |  | DNSP | Yes | 5 | 0.0027 | FALSE | FALSE | IR2190 waddamana 110/22 kV T1 transformer circuit tripped, under investigation. | No | Non-Critical | 20
36617 | 2191 | Jun 2017 | 2017-06-20 19:21 | 2017-06-20 19:36 | 15 | E1614 | KR-HR-KE 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 1053 | 0.5619 | 1 | 1 | IR2191 KR-HR-KE 110 kV transmission circuit tripped due to bark on line. | No | Non-Critical | 174
36700 | 2196 | Jul 2017 | 2017-07-26 10:56 | 2017-07-26 10:58 | 2 | E1652 | EL 110/11 kV T1 Transformer Circuit | Transformer | Fault | Pending Investigation | Transend | Yes | 11 | 0.0059 | FALSE | FALSE | IR2196 Electrona 110/11 kV T1 transformer circuit tripped during planned work for protection testing, with 5 MW loss of supply. | No | Non-Critical | 2
36787 | 2200 | Aug 2017 | 2017-08-11 21:50 | 2017-08-12 00:18 | 148 | E0864 | RB 44 kV C2 Feeder Circuit | Feeder | Fault | Unknown | MI | Yes | 14 | 0.0075 | FALSE | FALSE | IR2200 Rosebery C252 44kV feeder tripped with lightning in area. | No | Undefined | 148
36789 | 2203 | Sep 2017 | 2017-09-01 11:53 | 2017-09-01 12:24 | 31 | E0293 | AL 110/6.6 kV T1 Transformer Circuit | Transformer | Fault | Intertrip | Transend | Yes | 7 | 0.0037 | FALSE | FALSE | IR2203 Arthurs Lake T1 110/22 kV transformer circuit tripped due to inter trip signal from Hydro while attempting to start pumps. | No | Non-Critical | 31
36791 | 2205 | Sep 2017 | 2017-09-17 11:03 | 2017-09-17 11:14 | 11 | E0863 | RB 44 kV A2 Feeder Circuit | Feeder | Fault | Overload | Transend | Yes | 113 | 0.0603 | 1 | FALSE | IR2205 Rosebery 44 kV A252 feeder circuit was tripped following overload of T1 when T2 out of service for planned work. | No | Undefined | 11
36792 | 2206 | Sep 2017 | 2017-09-23 04:44 | 2017-09-23 04:49 | 5 | E2036 | FA-RB-NT-QT 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 8 | 0.0043 | FALSE | FALSE | IR2206 FA-RB-NT-QT 110 kV transmission circuit tripped with lightning in area causing loss of supply at Queenstown. | No | Not in WASP | 5
36793 | 2207 | Sep 2017 | 2017-09-23 14:54 | 2017-09-23 15:45 | 51 | E0401 | BU-PL 110 kV Transmission Circuit | Transmission | Fault | Protection & Control Device | Transend | Yes | 477 | 0.2545 | 1 | FALSE | IR2207 BU-PL 110 kV transmission circuit tripped. | No | Non-Critical | 50
36794 | 2208 | Sep 2017 | 2017-09-24 12:18 | 2017-09-26 20:25 | 3367 | E0785 | QU 110/22 kV T1 Transformer Circuit | Transformer | Fault | Cable Fault | Transend | Yes | 793 | 0.4232 | 1 | 1 | IR2208 Que T1 110/22 kV transformer circuit tripped due to cable fault | No | Non-Critical | 4087
36975 | 2212 | Oct 2017 | 2017-10-05 10:30 | 2017-10-05 10:34 | 4 | E0293 | AL 110/6.6 kV T1 Transformer Circuit | Transformer | Fault | Generator | Generator Request | Yes | 2 | 0.0011 | FALSE | FALSE | IR2212 Arthurs Lake T1 11/6.6 kV transformer tripped due to third party operator error | No | Non-Critical | 4
36977 | 2218 | Nov 2017 | 2017-11-13 09:52 | 2017-11-13 09:59 | 7 | E1703 | CO 220 kV Bus SPS | Bus | Fault | Human Error During Planned Work | Transend | Yes | 2233 | 1.1916 | 1 | 1 | IR2218 Bell Bay Aluminium AUFLS sheme inadvertantly tripped during planned work. | No | Not In Wasp | 7
37079 | 2222 | Nov 2017 | 2017-11-24 16:11 | 2017-11-24 16:13 | 2 | E0298 | AV-SM 110 kV Transmission Circuit | Transmission | Fault | Adverse Weather | Transend | Yes | 11 | 0.0059 | FALSE | FALSE | IR2222 AV-SM 110 kV transmission circuit tripped due to lightning. | No | Non-Critical | 2

## LOS
Loss of supply event frequency: > x, y system minutes
Performance Targets | Graph start | Cap | Target | Collar | Graph end
> 1.0 sysmins | 0 | 0 | 1 | 2 | 6
S Curve | 0.0015 | 0.0015 | 0 | -0.0015 | -0.0015
| slope | -0.0015
| intercept | 0.0015
Performance Targets | Graph start | Cap | Target | Collar | Graph end
> 0.1 sysmins | 0 | 0 | 4 | 8 | 15
S Curve | 0.0015 | 0.0015 | 0 | -0.0015 | -0.0015
| slope | -0.000375
| intercept | 0.0015
| Threshold X, Y = | > 0.1 sysmins | S Factor | > 1.0 sysmins | S Factor
| 2013 | 10 | -0.0015 | 1 | 0
| 2014 | 4 | 0 | 0 | 0.0015
| 2015 | 3 | 0.000375 | 0 | 0.0015
| 2016 | 1 | 0.001125 | 1 | 0
| 2017 | 4 | 0 | 1 | 0
| SUM |  | 0 |  | 0.003
| SD | 3.3615 |  | 0.54772
| Mean | 4.4 |  | 0.6

## LOS proposed
TasNetworks Loss of supply event frequency: > x, y system minutes
Performance Targets | Graph start | Cap | Target | Collar | Graph end
> 0.40 system minutes | 0 | 0 | 2 | 4 | 6
S Curve | 0.0015 | 0.0015 | 0 | -0.0015 | -0.0015
| slope | -0.00075
| intercept | 0.0015
| Threshold X, Y = | 0.05 | S Factor | 0.4 | Sfactor
| 2013 | 12 | -0.0015 | 4 | -0.0015
| 2014 | 5 | 0.000375 | 2 | 0
| 2015 | 4 | 0.00075 | 1 | 0.00075
| 2016 | 2 | 0.0015 | 1 | 0.00075
| 2017 | 6 | 0 | 3 | -0.00075
| SUM |  | 0.001125 |  | -0.00075
| SD | 3.7683 |  | 1.3038
| Mean | 5.8 |  | 2.2
Performance Targets | Graph start | Cap | Target | Collar | Graph end
> 0.05 system minutes | 0 | 2 | 6 | 10 | 15
S Curve | 0.0015 | 0.0015 | 0 | -0.0015 | -0.0015
| slope | -0.000375
| intercept | 0.00225

## LOS ptable
Request Instigator | Transend
Data
Start Time | Sum of LOS > X | Sum of LOS > Y
2013 | 12 | 4
2014 | 5 | 2
2015 | 4 | 1
2016 | 2 | 1
2017 | 6 | 3
Grand Total | 29 | 11
Calendar Year
|  |  | Threshold X= | 0.05 | 0.1 | 0.2 | 0.3 | 0.5 | 0.75 | 1
|  |  | 2013 | 12 | 10 | 8 | 4 | 2 | 1 | 1
|  |  | 2014 | 5 | 4 | 3 | 3 | 2 | 0 | 0
|  |  | 2015 | 4 | 3 | 3 | 3 | 1 | 1 | 0
|  |  | 2016 | 2 | 1 | 1 | 1 | 1 | 1 | 1
|  |  | 2017 | 6 | 4 | 4 | 3 | 2 | 1 | 1
|  |  | 5yav | 5.75 | 4.5 | 3.75 | 2.75 | 1.5 | 0.75 | 0.5

## AOD
AOD average outage duration
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 20 | 170 | 320 | 450
S Curve | 0.002 | 0.002 | 0 | -0.002 | -0.002
| slope | -1.3333e-05
| intercept | 0.0022667
| Results | minutes | S Factor
| 2013 | 161 | 0.00012
| 2014 | 201 | -0.00041333
| 2015 | 74 | 0.00128
| 2016 | 15 | 0.002
| 2017 | 411 | -0.002
| SUM |  | 0.00098667
| SD | 151.9335
| Mean | 172.4

## AOD ptable
Request Instigator | Transend
Average of LOS Duration
Start Time | Total
2013 | 160.9412
2014 | 200.7273
2015 | 73.5833
2016 | 15.0909
2017 | 410.5455
Grand Total | 169.5

## FaultOR
FaOR fault outage rate
Fault outage rate lines
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 12 | 19 | 26 | 40
S Curve | 0.002 | 0.002 | 0 | -0.002 | -0.002
| slope | -0.00028571
| intercept | 0.0054286
| Results | Percent | S Factor
| 2013 | 24.2 | -0.0014857
| 2014 | 15 | 0.0011429
| 2015 | 18.7 | 8.5714e-05
| 2016 | 26.2 | -0.002
| 2017 | 8.5 | 0.002
| SUM |  | -0.00025714
| SD | 7.1426
| Mean | 18.52
Fault outage rate transformer
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 6 | 10 | 14 | 20
S Curve | 0.002 | 0.002 | 0 | -0.002 | -0.002
| slope | -0.0005
| intercept | 0.005
| Results | Percent | S Factor
| 2013 | 15.5 | -0.002
| 2014 | 7.3 | 0.00135
| 2015 | 7.3 | 0.00135
| 2016 | 9.2 | 0.0004
| 2017 | 8.3 | 0.00085
| SUM |  | 0.00195
| SD | 3.4354
| Mean | 9.52
Fault outage rate reactive plant
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 0 | 13 | 26 | 40
S Curve | 0.001 | 0.001 | 0 | -0.001 | -0.001
| slope | -7.6923e-05
| intercept | 0.001
| Results | Percent | S Factor
| 2013 | 0 | 0.001
| 2014 | 33.3 | -0.001
| 2015 | 0 | 0.001
| 2016 | 0 | 0.001
| 2017 | 33.3 | -0.001
| SUM |  | 0.001
| SD | 18.2392
| Mean | 13.32

## ForcedOR
ForcedOR fault outage rate
Forced outage rate lines
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 5 | 10 | 15 | 25
S Curve | 0.001 | 0.001 | 0 | -0.001 | -0.001
| slope | -0.0002
| intercept | 0.002
| Results | Percent | S Factor
| 2013 | 6.5 | 0.0007
| 2014 | 8.4 | 0.00032
| 2015 | 6.5 | 0.0007
| 2016 | 17.8 | -0.001
| 2017 | 8.5 | 0.0003
| SUM |  | 0.00102
| SD | 4.7194
| Mean | 9.54
Forced outage rate transformer
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 7 | 12 | 17 | 20
S Curve | 0.001 | 0.001 | 0 | -0.001 | -0.001
| slope | -0.0002
| intercept | 0.0024
| Results | Percent | S Factor
| 2013 | 3.6 | 0.001
| 2014 | 15.6 | -0.00072
| 2015 | 12.8 | -0.00016
| 2016 | 10.1 | 0.00038
| 2017 | 15.6 | -0.00072
| SUM |  | -0.00022
| SD | 4.9918
| Mean | 11.54
Forced outage rate reactive plant
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 0 | 33 | 66 | 120
S Curve | 0.0005 | 0.0005 | 0 | -0.0005 | -0.0005
| slope | -1.5152e-05
| intercept | 0.0005
| Results | Percent | S Factor
| 2013 | 16.7 | 0.00024697
| 2014 | 116.7 | -0.0005
| 2015 | 25 | 0.00012121
| 2016 | 0 | 0.0005
| 2017 | 8.3 | 0.00037424
| SUM |  | 0.00074242
| SD | 47.5234
| Mean | 33.34
Note on A6: Author: Dummy s curve as weighting = 0%

## Faults
Outage Listing between 1/1/2017 and 12/31/2017
WASP Outage Key | Circuit Name | Circuit ID | Circuit Type | Circuit Voltage | Planned Open | Planned Close | Actual Open | Actual Close | Duration | MW min Lost | System Minutes | Description | Interruption Type | Primary Cause | Secondary Cause | Tertiary Cause | Failure of PS | Failure of SCADA | Incorrect Op | ITOMS Category | ITOMS Voltage | Instigator | Fault Location Asset ID | Fault Location | Failed Component | Weather | Sustained / Transient | Protection Problem | Contractor Error | Red Phase Fault | White Phase Fault | Blue Phase Fault | Earth Fault | Correct Lightning Tool Operation | SPS Operation | UFLS / UVLS Operation | NCSPS / FCSPS Operation | ScriptCalc Problem | Fire Start | Telecommunications Failure | WASP Data Finalised | Protection Type | Trip Mode | Phase | Notes
36013 | SH-PA-UL 110 kV Transmission Circuit | E1953 | Transmission | 110 |  |  | 2017-01-09 19:43 | 2017-01-09 19:43 | 0 | 0 | 0 | IR2169 SH-PA-UL 110 kV transmission circuit tripped and autoreclosed. | Fault | Unknown | Unknown |  | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36155 | CS-KI-KR 110 kV Transmission Circuit | E1955 | Transmission | 110 |  |  | 2017-02-19 21:32 | 2017-02-19 21:47 | 15 | 0 | 0 | IR2171 CS-KI-KR 110 kV transmission circuit tripped due to lightning. Norske skog and Nyrstar shed load due to power quality issues. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36238 | QU 110/22 kV T1 Transformer Circuit | E0785 | Transformer | 110/22 |  |  | 2017-03-09 06:33 | 2017-03-09 08:48 | 135 | 6 | 0.0032 | IR2172 Que T1 110/22 kV transformer tripped due to protection relay mal-operation. | Fault | Equipment Failure | Protection & Control Device |  | Yes | No | No | ITOMS – Transformer |  | Transend | QU-T1 | Power transformer |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36239 | GT-GC 220 kV Transmission Circuit | E1068 | Transmission | 220 |  |  | 2017-03-12 21:42 | 2017-03-12 22:21 | 39 | 0 | 0 | IR2173 Basslink tripped due to equipment failure at Loy Yang end. Load shed 387 MW by BBA, TEMCO, Nyrstar, Norske Skog. | Fault | Equipment Failure | Ancillary Equipment Failure |  | No | No | No |  |  | Basslink |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36240 | KI 110/33 kV T4 Transformer Circuit | E1852 | Transformer | 110/33 |  |  | 2017-03-13 03:55 | 2017-03-13 15:57 | 722 | 0 | 0 | IR2175 Kingston 110/33 kV T4 transformer circuit tripped due to restrricted earth fault operation caused by a cable termination failure on 33 kV side of T4 | Fault | Equipment Failure | Cable Fault |  | No | No | No | ITOMS – Transformer | 110KV | Transend | E1852 | KI 110/33 kV T4 Transformer Circuit |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  |  |  | A blue phase cable termination on 33 kV side of T4 (110/33 kV) was damaged.
36241 | GT 220 kV C2 Capacitor Circuit | E0505 | Capacitor | 220 |  |  | 2017-03-17 08:00 | 2017-03-18 16:22 | 1942 | 0 | 0 | IR2176 George Town 220 kV C2 capacitor circuit failed due to a faulty and bulging capacitor can. | Fault | Equipment Failure | Internal Fault |  | No | No | No | ITOMS – Compensation Equipment | 110KV | Transend | OG0666 | GT C2 |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  |  |  | A bulging capacitor can on top row of C2 was identified during visual inspection.
36242 | NW-SD 110 kV Transmission Circuit | E1497 | Transmission | 110 |  |  | 2017-03-26 05:17 | 2017-03-26 05:17 | 0 | 0 | 0 | IR2177 NW-SD 110 kV transmission circuit tripped and auto reclosed, pending investigation. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  |  |  | Norwood-Scottsdale 110 kV and Norwood-Scottsdale-Derby 110 kV transmission circuit tripped due to lightning strike.
36243 | HA 110/22 kV T4 Transformer Circuit | E1424 | Transformer | 110/22 |  |  | 2017-03-29 11:54 | 2017-03-31 18:04 | 3250 | 0 | 0 | IR2178 Hadspen 110/22 kV T4 transformer circuit tripped due to a cable termination failure on blue phase of secondary side (22 kV side) | Fault | Equipment Failure | Cable Fault |  | No | No | No | ITOMS – Transformer | 110KV | Transend | TRANNET | Transmission Network Parent Asset |  | Fine | Sustained | FALSE | FALSE | FALSE | FALSE | TRUE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  |  |  | Blue phase cable termination failed on secondary side (22 kV) of T4. At this point blue phase 22kV connection from T4 to D552 is supplied via two cables only. The other two phases still have three cable connections each.
36313 | BY 6.6 kV D3 Feeder Circuit | E0322 | Feeder | 6.6 |  |  | 2017-04-03 06:46 | 2017-04-03 06:58 | 12 | 171 | 0.0912 | IR2179 Boyer D352 circuit breaker tripped due to operational error causing loss of supply. | Fault | Operational | Human Error During Planned Work |  | No | No | Yes |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36314 | RI 110 kV C3 Capacitor Circuit | E1755 | Capacitor | 110 |  |  | 2017-04-06 17:51 | 2017-04-06 18:34 | 43 | 0 | 0 | IR2180 Risdon 110 kV C3 capacitor tripped due to failure of protection system. | Fault | Equipment Failure | Protection & Control Device |  | Yes | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36370 | PM-SH 220 kV Transmission Circuit | E0291 | Transmission | 220 |  |  | 2017-04-09 04:23 | 2017-04-09 04:23 | 0 | 0 | 0 | IR2181 PM-SH 220 kV transmission corcuit tripped at the same time as Basslink with lightning in area. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36370 | GT-GC 220 kV Transmission Circuit | E1068 | Transmission | 220 |  |  | 2017-04-09 04:23 | 2017-04-09 06:04 | 101 | 0 | 0 | IR2181 PM-SH 220 kV transmission corcuit tripped at the same time as Basslink with lightning in area. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36449 | HA 110/22 kV T4 Transformer Circuit | E1424 | Transformer | 110/22 |  |  | 2017-05-09 14:15 | 2017-05-17 14:11 | 11516 | 0 | 0 | IR2184 Hadspen 110/22 kV T4 transformer circuit tripped due to 22 kV cable failure. | Fault | Equipment Failure | Cable Fault |  | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36450 | SR 22 kV G2 Feeder Circuit | E1029 | Feeder | 22 |  |  | 2017-05-26 10:05 | 2017-05-26 10:39 | 34 | 329 | 0.1756 | IR2186 Savage River 22 kV G feeder tripped due to fault on customer section of feeder. | Fault | Third Party |  |  | No | No | No |  |  | MI |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36451 | GT-TV 3 220 kV Transmission Circuit | E1734 | Transmission | 220 |  |  | 2017-05-31 06:00 | 2017-05-31 07:54 | 114 | 0 |  | IR2187 Tamar Valley power station (internally) trippedcausing GCS operation and sheeding of load by Bell Bay Aluminium. | Fault | Third Party | Customer |  | No | No | No |  |  | Generator Request |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36619 | WA 110/22 kV T1 Transformer Circuit | E0951 | Transformer | 110/22 |  |  | 2017-06-09 10:40 | 2017-06-09 11:01 | 21 | 5 | 0.0027 | IR2190 Waddamana 110/22 kV T1 transformer circuit tripped due to fault on distribution feeder. | Fault | Third Party | DNSP |  | No | No | No |  |  | DNSP |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36617 | KR-HR-KE 110 kV Transmission Circuit | E1614 | Transmission | 110 |  |  | 2017-06-20 19:21 | 2017-06-20 19:36 | 15 | 1053 | 0.5619 | IR2191 KR-HR-KE 110 kV transmission circuit tripped due to bark on line. | Fault | Environmental | Adverse Weather | Wind / Waterborne Debris | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36617 | KR-HR-KE 110 kV Transmission Circuit | E1614 | Transmission | 110 |  |  | 2017-06-20 20:06 | 2017-06-20 22:45 | 159 | 0 | 0 | IR2191 KR-HR-KE 110 kV transmission circuit tripped due to bark on line. | Fault | Environmental | Adverse Weather | Wind / Waterborne Debris | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36620 | WA-BW 110 kV Transmission Circuit | E0001 | Transmission | 110 |  |  | 2017-06-26 09:23 | 2017-06-26 09:23 | 0 | 0 | 0 | IR2193 WA-BW 110 kV transmission line circuit tripped and auto reclosed due to wildlife. | Fault | Environmental | Wildlife | Bird(s) | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36699 | LF-RI 2 110 kV Transmission Circuit | E1072 | Transmission | 110 |  |  | 2017-07-18 09:03 | 2017-07-18 09:03 | 0 | 0 |  | IR2194 LF-RI 2 110 kV transmission line ciruit tripped and autoreclosed twice due to pollution combined with fog and caused load shedding at Nyrstar and Norske. | Fault | Environmental | Pollution | Industrial | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36700 | EL 110/11 kV T1 Transformer Circuit | E1652 | Transformer | 110/11 |  |  | 2017-07-26 10:56 | 2017-07-26 10:58 | 2 | 11 | 0.0059 | IR2196 Electrona 110/11 kV T1 transformer circuit tripped during planned work for protection testing, with 5 MW loss of supply. | Fault | Operational | Human Error During Planned Work | Maintenance Error | No | No | Yes |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36784 | NW-SD-DE 110 kV Transmission Circuit | E1635 | Transmission | 110 |  |  | 2017-08-11 21:48 | 2017-08-11 22:04 | 16 | 0 | 0 | IR2197 NW-SD-DE 110 kV transmission circuit tripped with lightning in area, also with DE-MR 110 kV transmission circuit. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36787 | RB 44 kV C2 Feeder Circuit | E0864 | Feeder | 44 |  |  | 2017-08-11 21:50 | 2017-08-12 00:18 | 148 | 14 | 0.0075 | IR2200 Rosebery C252 44kV feeder tripped with lightning in area. | Fault | Unknown | Unknown | Suspect Lightning | No | No | No |  |  | MI |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36785 | BU-HM 110 kV Transmission Circuit | E0400 | Transmission | 110 |  |  | 2017-08-11 22:28 | 2017-08-11 22:28 | 0 | 0 | 0 | IR2198 BU-HM 110 kV transmission circuit tripped and autoreclosed with lightning in area. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36788 | GT-TV 3 220 kV Transmission Circuit | E1734 | Transmission | 220 |  |  | 2017-08-21 13:29 | 2017-08-21 16:00 | 151 | 0 | 0 | IR2202 GT-TV 3 220 kV transmission circuit tripped due to intertrip from Tamar Valley power station. | Fault | Third Party | Intertrip |  | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36789 | AL 110/6.6 kV T1 Transformer Circuit | E0293 | Transformer | 110/6.6 |  |  | 2017-09-01 11:53 | 2017-09-01 12:24 | 31 | 7 | 0.0037 | IR2203 Arthurs Lake T1 110/22 kV transformer circuit tripped due to inter trip signal from Hydro while attempting to start pumps. | Fault | Third Party | Intertrip |  | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36790 | QT-NT 110 kV Transmission Circuit | E0721 | Transmission | 110 |  |  | 2017-09-06 00:27 | 2017-09-06 00:27 | 0 | 0 | 0 | IR2204 QT-NT 110 kV transmission circuit (disposed line) tripped with lightning in area. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36791 | RB 44 kV A2 Feeder Circuit | E0863 | Feeder | 44 |  |  | 2017-09-17 11:03 | 2017-09-17 11:14 | 11 | 113 | 0.0603 | IR2205 Rosebery 44 kV A252 feeder circuit was tripped following overload of T1 when T2 out of service for planned work. | Fault | Operational | Overload |  | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36792 | FA-RB-NT-QT 110 kV Transmission Circuit | E2036 | Transmission | 110 |  |  | 2017-09-23 04:44 | 2017-09-23 04:49 | 5 | 8 | 0.0043 | IR2206 FA-RB-NT-QT 110 kV transmission circuit tripped with lightning in area causing loss of supply at Queenstown. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36793 | BU-PL 110 kV Transmission Circuit | E0401 | Transmission | 110 |  |  | 2017-09-23 14:54 | 2017-09-23 15:45 | 51 | 477 | 0.2545 | IR2207 BU-PL 110 kV transmission circuit tripped. | Fault | Equipment Failure | Protection & Control Device |  | Yes | Yes | No |  |  | Transend | E0401 | BU-PL 110 kV Transmission Circuit |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36795 | NW-SD 110 kV Transmission Circuit | E1497 | Transmission | 110 |  |  | 2017-09-24 03:27 | 2017-09-24 12:49 | 562 | 0 | 0 | IR2209 NW-SD 110 kV transmission circuit tripped, reclosed and tripped. | Fault | Unknown | Unknown | Unknown | No | No | No | ITOMS - Overhead Lines | 110KV | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  |  |  | Norwood-Scottsdale transmission circuit tripped due to unknown reason and successfully auto reclosed after 8 seconds. As a result of transmission circuit tripping Derby D199NC runback scheme activated and reduced MRWF generation to acceptable level.
36794 | QU 110/22 kV T1 Transformer Circuit | E0785 | Transformer | 110/22 |  |  | 2017-09-24 12:18 | 2017-09-26 20:25 | 3367 | 793 | 0.4232 | IR2208 Que T1 110/22 kV transformer circuit tripped due to cable fault | Fault | Equipment Failure | Cable Fault |  | No | No | No | ITOMS – Transformer | 110KV | Transend | E0785 | QU 110/22 kV T1 Transformer Circuit |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36970 | HA 110/22 kV T4 Transformer Circuit | E1424 | Transformer | 110/22 |  |  | 2017-09-28 15:32 | 2017-11-29 14:01 | 89189 | 0 | 0 | IR2210 Hadspen T4 tripped due to 22 kV cable failure (B phase) on transformer termination box | Fault | Equipment Failure | Poor Workmanship |  | No | No | No | ITOMS – Transformer | 110KV | Transend | E1424 | HA 110/22 kV T4 Transformer Circuit |  | Fine | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36971 | BU-PL 110 kV Transmission Circuit | E0401 | Transmission | 110 |  |  | 2017-10-01 16:49 | 2017-10-01 16:49 | 0 | 0 | 0 | IR2211 Burnie-Port Latta 110 kV transmission circuit tripped and successfully auto reclosed | Fault | Unknown | Unknown |  | No | No | No | ITOMS - Overhead Lines | 110KV | Transend | E0401 | BU-PL 110 kV Transmission Circuit |  | Fine | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36975 | AL 110/6.6 kV T1 Transformer Circuit | E0293 | Transformer | 110/6.6 |  |  | 2017-10-05 10:30 | 2017-10-05 10:34 | 4 | 2 | 0.0011 | IR2212 Arthurs Lake T1 11/6.6 kV transformer tripped due to third party operator error | Fault | Third Party | Generator |  | No | No | No | ITOMS – Transformer | 110KV | Generator Request | E0293 | AL 110/6.6 kV T1 Transformer Circuit |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36976 | BU 110 kV C1 Capacitor Circuit | E1392 | Capacitor | 110 |  |  | 2017-10-05 21:40 | 2017-10-11 13:29 | 8149 | 0 | 0 | IIR 2213 Burnie Capacitor C1 failed (blue phase) and tripped circuit breaker F652. The capacitor circuit was out of service for approximately 6 days | Fault | Equipment Failure | Internal Fault |  | No | No | No | ITOMS – Compensation Equipment | 110KV | Transend | BU-F652 | Circuit breaker |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36972 | LI-CS 2 220 kV Transmission Circuit | E0026 | Transmission | 220 |  |  | 2017-10-17 02:50 | 2017-10-17 02:50 | 0 | 0 | 0 | IR2214 Liapootah-Chapel Street No 2 220 kV transmission circuit tripped and successfuly auto reclosed | Fault | Unknown | Unknown |  | No | No | No | ITOMS - Overhead Lines | 220kV | Transend | E0026 | LI-CS 2 220 kV Transmission Circuit |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36973 | PO-PM 3 220 kV Transmission Circuit | E0261 | Transmission | 220 |  |  | 2017-10-24 15:25 | 2017-10-25 11:14 | 1189 | 0 | 0 | IR 2215 Poatina-Palmerston No 3 220 kV transmission circuit tripped due to intertrip signal sent from Poatina Power Station | Fault | Third Party | Generator |  | No | No | No | ITOMS - Overhead Lines | 220kV | Generator Request | E0261 | PO-PM 3 220 kV Transmission Circuit |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
36977 | CO 220 kV Bus SPS | E1703 | Bus | 220 |  |  | 2017-11-13 09:52 | 2017-11-13 09:59 | 7 | 2233 | 1.1916 | IR2218 Bell Bay Aluminium AUFLS sheme inadvertantly tripped during planned work. | Fault | Operational | Human Error During Planned Work | Testing Error | No | No | Yes |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
37078 | SH-FA 1 220 kV Transmission Circuit | E0538 | Transmission | 220 |  |  | 2017-11-24 13:42 | 2017-11-24 13:48 | 6 | 0 | 0 | IR2221 SH-FA 1 & 2 220 kV transmission circuits tripped due to lightning. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
37078 | SH-FA 2 220 kV Transmission Circuit | E0539 | Transmission | 220 |  |  | 2017-11-24 13:42 | 2017-11-24 13:48 | 6 | 0 | 0 | IR2221 SH-FA 1 & 2 220 kV transmission circuits tripped due to lightning. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
37079 | AV-SM 110 kV Transmission Circuit | E0298 | Transmission | 110 |  |  | 2017-11-24 16:11 | 2017-11-24 16:13 | 2 | 11 | 0.0059 | IR2222 AV-SM 110 kV transmission circuit tripped due to lightning. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
37080 | FA 220/110 kV T2 Transformer Circuit | E0705 | Transformer | 220/110 |  |  | 2017-12-07 15:31 | 2017-12-07 15:35 | 4 | 0 | 0 | IR2223 Farrell 220/110 kV T2 transformer circuit tripped, Cause is pending investigation. | Fault | Operational | Human Error During Planned Work |  | No | No | Yes |  |  | Transend |  |  |  |  | Sustained | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
37133 | PM-SH 220 kV Transmission Circuit | E0291 | Transmission | 220 |  |  | 2017-12-24 03:51 | 2017-12-24 03:51 | 0 | 0 | 0 | IR2225 PM-SH 220 kV transmission circuit tripped due to lightning. | Fault | Environmental | Adverse Weather | Lightning | No | No | No |  |  | Transend |  |  |  |  | Transient | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE

## POEquipment
Proper Operation of Equipment
Failure of protection system
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 0 | 4 | 8 | 14
S Curve | 0.001 | 0.001 | 0 | -0.001 | -0.001
| slope | -0.00025
| intercept | 0.001
| Results | Events | S Factor
| 2013 | 13 | -0.001
| 2014 | 0 | 0.001
| 2015 | 4 | 0
| 2016 | 1 | 0.00075
| 2017 | 3 | 0.00025
| SUM |  | 0.001
| SD | 5.1672
| Mean | 4.2
Material failure of SCADA
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 2 | 3 | 4 | 6
S Curve | 0.001 | 0.001 | 0 | -0.001 | -0.001
| slope | -0.001
| intercept | 0.003
| Results | Events | S Factor
| 2013 | 2 | 0.001
| 2014 | 2 | 0.001
| 2015 | 2 | 0.001
| 2016 | 4 | -0.001
| 2017 | 4 | -0.001
| SUM |  | 0.001
| SD | 1.0954
| Mean | 2.8
Incorrect operational isolation
Performance Targets | Graph start | Cap | Target | Collar | Graph end
minutes | 0 | 2 | 4 | 6 | 8
S Curve | 0.0005 | 0.0005 | 0 | -0.0005 | -0.0005
| slope | -0.00025
| intercept | 0.001
| Results | Events | S Factor
| 2013 | 2 | 0.0005
| 2014 | 4 | 0
| 2015 | 6 | -0.0005
| 2016 | 6 | -0.0005
| 2017 | 4 | 0
| SUM |  | -0.0005
| SD | 1.6733
| Mean | 4.4

## PO of Equipment
TasNetworks
Parameter | Failure protection system | Material failure of SCADA | Incorrect Isolation
2011
2012
2013 | 13 | 2 | 2
2014 | 0 | 2 | 4
2015 | 4 | 2 | 6
2016 | 1 | 4 | 6
2017 | 3 | 4 | 4
Target (5 year av) | 4.2 | 2.8 | 4.4

## MIC
Past submissions
[5 empty] | Capped unplanned count | Adjusted performance count
Regulatory Period | CYear | Planned | Unplanned | Total (Planned + Unplanned) | Min of Raw Unplanned or 0.17 x (M) | planned + capped unplanned
(RP) |  | (a) | (b) | (a) + (b) | (d) | (e)
RP 2009-14 | 2011 | 667 | 62 | 729 | 62 | 729
RP 2009-14 | 2012 | 1387 | 42 | 1429 | 42 | 1429 | from result letter
RP 2009-14 | 2013 | 1696 | 64 | 1760 | 64 | 1760 | from audited template
RP 2014-19 | 2014 | 1122 | 108 | 1230 | 108 | 1230 | from 2017 YTD
RP 2014-19 | 2015 | 160 | 87 | 247 | 87 | 247
RP 2014-19 | 2016 | 2380 | 597 | 2977 | 267 | 2647
RP 2014-19 | YTD 2017 | 2431 | 271 | 2702 | 267 | 2698
Max |  |  |  | 2977
Min |  |  |  | 247
Average of 5 median |  |  | M = | 1570 | T = | 1559
Unplanned outage event limit (0.17 * M) = |  |  | 266.9
Dollars per Dispatch Interval ($/DI) = |  | 1090.4426
MAR = |  | 170000000

## LOS thresholds
Version 4 (current period for TN) |  |  |  | Version 5 (RR19) |  |  | Current targets | Revenue at risk
TNSP | X threshold | Y threshold |  | TNSP | X threshold | Y threshold
TasNetworks | 0.1 | 1 |  | TasNetworks v4 | 0.1 | 1 | (10 and 3) | +/- 0.3% AR
Powerlink | 0.1 | 0.75 |  | Powerlink | 0.05 | 0.4 | (4 and 1) | +/- 0.3% AR
Electranet | 0.05 | 0.2 |  | Electranet | 0.05 | 0.2 | (7 and 2) | +/- 0.3% AR
Transgrid | 0.05 | 0.25 |  | Transgrid | 0.05 | 0.25 | (4 and 1) | +/- 0.3% AR
Ausnet | 0.05 | 0.3 |  | Ausnet | 0.05 | 0.3 | (2 and 1) | +/- 0.3% AR
YTD 2017
TasNetworks
Threshold X, Y = | 0.05 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 1
2011 | 7 | 7 | 5 | 4 |  | 4 | 3
2012 | 18 | 10 | 9 | 7 | 6 | 5 | 2
2013 | 12 | 10 | 8 | 4 | 4 | 2 | 1
2014 | 5 | 4 | 3 | 3 | 2 | 2 | 0
2015 | 4 | 3 | 3 | 3 | 1 | 1 | 0
2016 | 2 | 1 | 1 | 1 | 1 | 1 | 1
YTD 2017 | 1 | 1 | 1 | 1 | 1 | 1 | 0
5 year av 12-16 | 8.2 | 5.6 | 4.8 | 3.6 | 2.8 | 2.2 | 0.8
5 year av 13-17 | 4.8 | 3.8 | 3.2 | 2.4 | 1.8 | 1.4 | 0.4
5 year total | 41 | 28 | 24 | 18 |  | 11 | 4
Notes
2014-16 results may be extraordinary
0.05 seems a reasonable lower threshold given that three of the 4 other TNSPs use this and the average of eight events gives room for improvement
0.5 seems a reasonable upper threshold given that it results in an average of two events per year
Note that the current thresholds of 0.1 and 1.0 still give workable targets of 4 and 0.5 respectively
LEOY |  | No events for various thresholds
TasNetworks
Threshold X, Y = | 0.05 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 1
2011 | 7 | 7 | 5 | 4 |  | 4 | 3
2012 | 18 | 10 | 9 | 7 | 6 | 5 | 2
2013 | 12 | 10 | 8 | 4 | 4 | 2 | 1
2014 | 5 | 4 | 3 | 3 | 2 | 2 | 0
2015 | 4 | 3 | 3 | 3 | 1 | 1 | 0
2016 | 2 | 1 | 1 | 1 | 1 | 1 | 1
2017 | 6 | 4 | 4 | 3 | 2 | 1 | 1
5 year av 12-16 | 8.2 | 5.6 | 4.8 | 3.6 | 2.8 | 2.2 | 0.8
Target (5 year av) | 5.8 | 4.4 | 3.8 | 2.8 | 2 | 1.4 | 0.6
| SD | 3.7683 |  |  | SD | 1.2247