## R24 Targets
Transmission service component caps, floors and targets
Parameters | Distribution | Cap | Target | Floor | Weighting
Average circuit outage rate
Lines event rate - fault | Log Normal | 8.99% | 14.65% | 22.14% | 0.2%
Tranformer event rate - fault | Uniform | 3.83% | 7.31% | 10.79% | 0.2%
Reactive plant outage rate - fault | Normal | 4.06% | 17.44% | 30.81% | 0.1%
Lines event rate - forced | Log Normal | 6.88% | 15.98% | 30.16% | 0.1%
Transformer outage rate - forced | Log Normal | 2.31% | 6.59% | 13.79% | 0.1%
Reactive plant outage rate - forced | Log Normal | 8.63% | 15.51% | 25.23% | 0.05%
Loss of supply events
LOS > 0.1 system minutes | Poisson | 1 | 4 | 7 | 0.15%
LOS > 1 system minutes | Poisson | 0 | 0 | 2 | 0.15%
Average outage duration (minutes) | Log Normal | 15.71 | 170.67 | 643.39 | 0.2%
Proper operation of equipment
Failure of protection system | Weibull | 1 | 3 | 6 | 0%
Material failure of SCADA | Poisson | 0 | 2 | 4 | 0%
Incorrect operational isolation | Exponential | 0 | 3 | 8 | 0%
Transmission MIC parameter values
Calendar year | Performance count
Target | 1967.8
Cap for unplanned outages | 343.162
Dollar per dispatch interval | 810.8914
Note
Kolmogorov-Smirnov Goodness-of-Fit Test

## Fault COR
Lines outage rate - Fault
Calendar year | Event rate (%)
2017 | 9.3897
2018 | 15.8879
2019 | 21.6981
2020 | 13.2075
2021 | 13.0841
Distribution | Cap | Target | Floor
Log Normal | 8.9922 | 14.6535 | 22.1425
Transformers outage rate - Fault
Calendar year | Event rate (%)
2017 | 8.2569
2018 | 10
2019 | 8.2569
2020 | 5.5046
2021 | 4.5455
Distribution | Cap | Target | Floor
Uniform | 3.8331 | 7.3128 | 10.7925
Reactive plant outage rate - Fault
Calendar year | Event rate (%)
2017 | 33.3333
2018 | 23.0769
2019 | 0
2020 | 23.0769
2021 | 7.6923
Distribution | 1 SD | Cap | Target | Floor
Normal | 13.3727 | 4.0632 | 17.4359 | 30.8086

## Forced COR
Lines outage rate - Forced
Calendar year | Event rate (%)
2017 | 7.5117
2018 | 12.1495
2019 | 30.1887
2020 | 14.1509
2021 | 15.8879
Distribution | Cap | Target | Floor
Log Normal | 6.8767 | 15.9777 | 30.1563
Transformers outage rate - Forced
Calendar year | Event rate (%)
2017 | 13.7615
2018 | 7.2727
2019 | 4.5872
2020 | 4.5872
2021 | 2.7273
Distribution | Cap | Target | Floor
Log Normal | 2.3123 | 6.5872 | 13.7923
Reactive plant outage rate - Forced
Calendar year | Event rate (%)
2017 | 8.3333
2018 | 15.3846
2019 | 15.3846
2020 | 15.3846
2021 | 23.0769
Distribution | Cap | Target | Floor
Log Normal | 8.6332 | 15.5128 | 25.2333

## LOS
LOS > 0.1 sys mins
Calendar year | No. of events
2017 | 4
2018 | 2
2019 | 2
2020 | 8
2021 | 2
Distribution | Cap | Target | Floor
Poisson | 1 | 4 | 7
LOS > 1 sys mins
Calendar year | No. of events
2017 | 1
2018 | 0
2019 | 1
2020 | 0
2021 | 0
Distribution | Cap | Target | Floor
Poisson | 0 | 0 | 2

## AOD
AOD
Calendar year | Duration (mins)
2017 | 410.4545
2018 | 45.9091
2019 | 273
2020 | 105
2021 | 19
Distribution | Cap | Target | Floor
Log Normal | 15.713 | 170.6727 | 643.3866

## POE
Failure of protection system
Calendar year | No. of events
2017 | 4
2018 | 1
2019 | 2
2020 | 4
2021 | 5
Distribution | Cap | Target | Floor
Weibull | 1 | 3 | 6
Material failure of SCADA
Calendar year | No. of events
2017 | 4
2018 | 4
2019 | 0
2020 | 0
2021 | 1
Distribution | Cap | Target | Floor
Poisson | 0 | 2 | 4
Incorrect operational isolation
Calendar year | No. of events
2017 | 3
2018 | 6
2019 | 1
2020 | 1
2021 | 2
Distribution | Cap | Target | Floor
Exponential | 0 | 3 | 8

## MIC
Calendar year | Unplanned | Planned | Total (Planned + Unplanned) | Capped Unplanned count | Adjusted performance count (Planned + Capped Unplanned) | Comments
2015 | 87 | 160 | 247 | 87 | 247
2016 | 597 | 2267 | 2864 | 343 | 2610 | 113 WA-BW planned events - Exclusion '9' applied
2017 | 271 | 2431 | 2702 | 271 | 2702
2018 | 224 | 3905 | 4129 | 224 | 4129 | 131 WA-BW planned events - Exclusion '9' applied
2019 | 59 | 1696 | 1755 | 59 | 1755
2020 | 26 | 1368 | 1394 | 26 | 1394
2021 | 151 | 1227 | 1378 | 151 | 1378
Min |  |  | 247
Max |  |  | 4129
Average of 5 median |  | M | 2018.6 | T | 1967.8
Unplanned outage event limit (0.17*M) | 343.162
MAR ($) | 159567215.2221 | Smoothed MAR (2024/25)
Dollars per Dispatch Interval ($/DI) | 810.8914
Target | 1967.8